## Test1a
Test 1a | Sizing of one borehole based on a balanced ground load for a ten year period with two peak durations (1 and 6 hours) | [14 empty] | Peak load duration of 6 hours | [5 empty] | Peak load duration of 1 hour
[16 empty] | Rb calculated by tool |  |  | Imposed Rb |  |  | Rb calculated by tool |  |  | Imposed Rb
Hourly ground load |  | Month | Ground monthly averaged load | Ground monthly peak cooling load | Peak cooling hours | Ground monthly peak heating load | Peak heating hours |  | Ground yearly, monthly and hourly pulses | Parameter | Value | Units |  | Level | Sizing tool | Borehole length | Difference from mean | Rb calculated by tool | Borehole length | Difference from mean | Imposed Rb=0.13 m.k.W-1 | Borehole length | Difference from mean | Rb calculated by tool | Borehole length | Difference from mean | Imposed Rb=0.13 m.k.W-1
(W) |  |  | (W) | (W) | (hr) | (W) | (hr) |  | (W) | Nb | 1 | ---- |  |  |  | (m) | % | (m.K/W) | m | % | (m.K/W) | (m) | % | (m.K/W) | m | % | (m.K/W)
qh |  |  | qm | qh,C | th,C | qh,H | th,H |  | Cooling | B | 6 | m | A | L2 | Classic ASHRAE sizing equation | 61.7 | 5.2067 | 0.122 | 63.7 | 6.1667 | 0.13 | 51.3 | 9.2026 | 0.122 | 53.4 | 10.5062 | 0.13
0.01 |  | 1 | 603.6193 | 0.01 | 1 and 6 | 4400.864 | 1 and 6 | qh | -4427.9014 | D | 4 | m | B | L2 | Modified ASHRAE sizing equation | 62.1 | 5.8888 | 0.127 | 62.7 | 4.5 | 0.13 | ----- | ----- | ----- | ----- | ----- | -----
0.01 |  | 2 | 491.6402 | 0.01 | 1 and 6 | 3706.6449 | 1 and 6 | qm | -648.2689 | rb | 75 | mm | C | L2 | Modified + ASHRAE sizing equation -B | 60.7 | 3.5016 | 0.122 | 62.7 | 4.5 | 0.13 | 50.8 | 8.1382 | 0.122 | 52.8 | 9.2646 | 0.13
0.01 |  | 3 | 202.2316 | -0.01 | 1 and 6 | 2208.4064 | 1 and 6 | qy | -0.90244 | rp,o,rp,i | 16.7, 13.7 | mm | D | L2 | Modified + ASHRAE sizing equation- F | 60.7 | 3.5016 | 0.122 | 62.7 | 4.5 | 0.13 | 50.8 | 8.1382 | 0.122 | 52.8 | 9.2646 | 0.13
0.01 |  | 4 | -168.0881 | -2002.0333 | 1 and 6 | 58.6726 | 1 and 6 |  | Heating | 2dp | 75 | mm | E | L2 | Alternative method | 57.8 | -1.4433 | 0.122 | 59.8 | -0.33333 | 0.13 | 44.9 | -4.4212 | 0.122 | 46.9 | -2.9449 | 0.13
0.01 |  | 5 | -430.4907 | -3605.0519 | 1 and 6 | -0.01 | 1 and 6 | qh | 4427.0813 | mf | 0.1 | kg.s-1.kW-1 | Est | L2 | Alternative method (short-term effects) | 54.8 | -6.5587 | 0.122 | 56.6 | -5.6667 | 0.13 | 38.7 | -17.6191 | 0.121 | 40 | -17.2238 | 0.13 | Impact of peak load magnitude on short-term effects, all lengths in m
0.01 |  | 6 | -685.3155 | -4386.6301 | 1 and 6 | -0.01 | 1 and 6 | qm | 679.7949 | ρf | 1052 | kg.m-3 | F | L2 | GHX design tool box | 58 | -1.1022 | 0.126 | 59 | -1.6667 | 0.13 | 42 | -10.5944 | 0.122 | 43 | -11.0156 | 0.13 |  | th=6 hr, Rb=0.13 m.K/W |  |  | th=1 hr, Rb=0.13 m.K/W
493.8584 |  | 7 | -648.2689 | -4427.9014 | 1 and 6 | -0.01 | 1 and 6 | qy | -0.90244 | cp,f | 3795 | J.kg-1.K-1 | G | L3 | Modified Ashrae sizing equation -B (monthly) | 60.7 | 3.5016 | 0.12 | 62.6 | 4.3333 | 0.13 | 50.8 | 8.1382 | 0.122 | 52.7 | 9.0576 | 0.13 |  | qh (W) |  |  | qh (W)
861.1247 |  | 8 | -477.8342 | -3726.4853 | 1 and 6 | -0.01 | 1 and 6 |  |  | μf | 0.0052 | kg.s-1.m-1 | H | L3 | Alternative method (monthly) | 57.8 | -1.4433 | 0.12 | 59.7 | -0.5 | 0.13 | 44.8 | -4.634 | 0.12 | 46.8 | -3.1519 | 0.13 |  | -2213.9507 | -4427.9014 | -8855.8029 | -2213.9507 | -4427.9014 | -8855.8029
1088.1919 |  | 9 | -186.4283 | -2136.8185 | 1 and 6 | 0.01 | 1 and 6 |  |  | kf | 0.48 | W.m-1.K-1 | Hst | L3 | Alternative method (monthly,short-term effects) | 54.8 | -6.5587 | 0.12 | 56.5 | -5.8333 | 0.13 | 38.7 | -17.6191 | 0.12 | 39.9 | -17.4308 | 0.13 | E | 33.7 | 57.8 | 101.9 | 29.3 | 46.9 | 78.5
1177.2826 |  | 10 | 159.7481 | -7.0147 | 1 and 6 | 1967.9599 | 1 and 6 |  |  | ρcp,g | 2073.6 | kJ.m-3.K-1 | I | L3 | EED monthly v.4.17 | 59.8 | 1.967 | 0.127 | 60 | -1.1842e-14 | 0.13 | 43.9 | -6.5499 | 0.127 | 44.1 | -8.7393 | 0.13 | Est | 32.5 | 54.8 | 95.6 | 26.4 | 40 | 64.4
1144.4877 |  | 11 | 478.228 | 0.01 | 1 and 6 | 3746.0496 | 1 and 6 |  |  | ρcp,gr | 3900 | kJ.m-3.K-1 | J | L3 | GLHEpro monthly v 5.0 | 56.65 | -3.4042 | 0.127 | 57.3 | -4.5 | 0.13 | 38.5 | -18.0449 | 0.127 | 39.1 | -19.0863 | 0.13 | J | 33.9 | 57.3 | 98.5 | 26.2 | 39.1 | 62.7
1016.4292 |  | 12 | 679.7949 | 0.01 | 1 and 6 | 4427.0813 | 1 and 6 |  |  | ρcp,pipe | 1540 | kJ.m-3.K-1 | K | L4 | EED hourly v.4.17 | 56.8 | -3.1484 | 0.127 | 57 | -5 | 0.13 | 56.8 | 20.9104 | 0.127 | 57 | 17.9561 | 0.13 | Dif % (E,Est) | 3.5608 | 5.1903 | 6.1825 | 9.8976 | 14.7122 | 17.9618
826.0423 | [9 empty] | αg | 0.075 | m2.day-1 | L | L4 | DST | 58.7 | 0.091346 | 0.125 | 59.7 | -0.5 | 0.13 | 58.7 | 24.955 | 0.125 | 59.7 | 23.5435 | 0.13
608.0424 | [9 empty] | kg | 1.8 | W.m-1.K-1 | X |  | Your tool
394.6362 | [9 empty] | kgr | 1.4 | W.m-1.K-1
211.9783 | [9 empty] | Tg | 17.5 | °C
77.7415 | [9 empty] | kp | 0.43 | W.m-1.K-1
0.01 | [9 empty] | TL | 0 | °C
0.01 | [9 empty] | TH | 35 | °C |  |  | Mean | 58.6464 |  | 0.1235 | 60 |  |  | 46.9769 |  | 0.123 | 48.3231
1.1005 | [9 empty] | Rb | 0.13 | m.K.W-1 |  |  | Min | 54.8 |  | 0.12 | 56.5 |  |  | 38.5 |  | 0.12 | 39.1
56.0136 | [9 empty] | t | 10 | years |  |  | Max | 62.1 |  | 0.127 | 63.7 |  |  | 58.7 |  | 0.127 | 59.7
124.8147 | [9 empty] | Rc | 0 | m.K.W-1
190.287 | [9 empty] | hconv | 1000 | W.m-2.K-1
238.0461 | [9 empty] | q''g | 0 | W/m2
258.4726 | [9 empty] | Fsc | 1.04 | -----
247.7521 | [9 empty] | COPC | ----- | -----
207.9404 | [9 empty] | COPH | ----- | -----
146.1164
72.8132
0.01
0.01
0.01
0.01
0.01
0.01
0.01
19.3225
59.6084
82.4894
81.2655
53.2038
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
60.5
97.153
107.3705
92.8704
59.3293
15.3899
0.01
0.01
0.01
0.01
0.01
0.01
58.2846
117.8015
167.7752
198.6935
204.2203
182.6893
137.9121
79.117
19.9536
0.01
0.01
0.01
88.3375
230.8492
418.8898
634.5698
851.8859
1039.1212
1162.3217
1189.4858
1094.9797
863.6311
493.9506
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
1047.1327
2066.0831
2974.6407
3697.5748
4173.4694
4360.2943
4239.186
3816.0946
3121.1768
2206.0425
1139.1751
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
1002.6117
1923.8624
2706.3318
3302.1612
3675.3866
3803.5984
3678.9505
3308.5293
2714.0848
1931.1114
1007.252
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
1150.6224
2228.0766
3152.018
3853.2275
4279.6187
4400.864
4211.1596
3729.8093
2999.5219
2082.5493
1055.0196
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
489.9793
854.2866
1079.4567
1167.7308
1135.1033
1008.0072
819.1266
602.8994
391.2643
210.1489
77.0639
0.01
0.01
1.0907
55.5061
123.6729
188.5299
235.8274
256.0412
245.4002
205.9485
144.7042
72.1032
0.01
0.01
0.01
0.01
0.01
0.01
0.01
19.1208
58.9809
81.6139
80.396
52.63
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
59.7744
95.9793
106.0641
91.7324
58.5973
15.1988
0.01
0.01
0.01
0.01
0.01
0.01
57.5252
116.2562
165.5598
196.0526
201.4884
180.2296
136.0434
78.0382
19.6799
0.01
0.01
0.01
87.0947
227.5813
412.9237
625.4769
839.6053
1024.0514
1145.3647
1172.0294
1078.8156
850.8074
486.5734
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
1030.2236
2032.5407
2926.0901
3636.9041
4104.6281
4287.9932
4168.5253
3752.1552
3068.6101
2168.697
1119.7916
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
984.3327
1888.6202
2656.5205
3241.0962
3607.1
3732.5988
3609.9576
3246.1951
2662.7141
1894.3924
988.0121
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
1127.24
2182.6041
3087.4138
3773.9149
4191.1559
4309.5109
4123.3767
3651.7346
2936.472
2038.5923
1032.6589
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
478.9944
835.0592
1055.0669
1141.244
1109.2572
984.9666
800.3317
589.013
382.2182
205.2718
75.2688
0.01
0.01
1.0652
54.1937
120.7377
184.0388
230.1888
249.8968
239.4895
200.97
141.1935
70.3477
0.01
0.01
0.01
0.01
0.01
0.01
0.01
18.642
57.4982
79.5549
78.3606
51.2931
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
58.182
93.4138
103.2196
89.2642
57.0155
14.7874
0.01
0.01
0.01
0.01
0.01
0.01
55.9316
113.025
160.9435
190.5686
195.8344
175.1562
132.2018
75.8277
19.1209
0.01
0.01
0.01
84.589
221.0131
400.9693
607.3131
815.1483
994.1305
1111.797
1137.5759
1047.006
825.645
472.1399
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
998.3738
1969.5214
2835.1039
3523.4892
3976.2595
4153.5054
4037.4106
3633.8001
2971.5408
2099.9001
1084.1683
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
951.7784
1825.9883
2568.183
3133.0271
3486.5013
3607.4671
3488.6112
3136.783
2572.7274
1830.1999
954.4436
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
1087.5099
2105.4785
2978.0344
3639.8711
4041.9109
4155.6589
3975.7944
3520.7005
2830.8359
1965.0707
995.3221
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
461.063
803.7215
1015.376
1098.2065
1067.3241
947.6417
769.93
566.5845
367.6291
197.418
72.3823
0.01
0.01
1.0245
52.0956
116.0517
176.8787
221.212
240.1283
230.1058
193.077
135.6353
67.5721
0.01
0.01
0.01
0.01
0.01
0.01
0.01
17.8929
55.1817
76.3424
75.189
49.2124
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
55.746
89.4937
98.8784
85.5016
54.607
14.1617
0.01
0.01
0.01
0.01
0.01
0.01
53.527
108.1549
153.9932
182.3211
187.3406
167.5428
126.4431
72.5178
18.2848
0.01
0.01
0.01
80.8567
211.2398
383.2
580.3419
778.8698
949.7922
1062.1056
1086.6246
1000.0123
788.5087
450.8592
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
952.0451
1877.9392
2703.0015
3358.9748
3790.225
3958.7813
3847.7432
3462.7458
2831.3768
2000.6494
1032.822
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
905.4211
1736.875
2442.6004
2979.5212
3315.3397
3430.0181
3316.6711
2981.8796
2445.4297
1739.465
907.0333
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
1032.0083
1997.8182
2825.4661
3453.04
3834.048
3941.5395
3770.553
3338.6074
2684.1457
1863.0506
943.5508
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
436.4452
760.728
960.9597
1039.2423
1009.9123
896.5737
728.3625
535.9393
347.7085
186.7012
68.4462
0.01
0.01
0.96899
49.2421
109.6828
167.1537
209.0272
226.8775
217.3851
182.3841
128.1102
63.8167
0.01
0.01
0.01
0.01
0.01
0.01
0.01
16.8846
52.0652
72.0228
70.9272
46.4182
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
52.5017
84.2759
93.1032
80.4991
51.4068
13.3307
0.01
0.01
0.01
0.01
0.01
0.01
50.3463
101.7163
144.8098
171.4295
176.1299
157.4997
118.8509
68.1562
17.1836
0.01
0.01
0.01
75.9519
198.403
359.8734
544.9543
731.2958
891.6796
997.0111
1019.9148
938.516
739.9372
423.0401
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
891.9095
1759.1222
2531.6989
3145.7469
3549.2228
3706.6449
3602.2739
3241.473
2650.1508
1872.3843
966.4973
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
845.9329
1622.5727
2281.594
2782.8049
3096.0972
3202.8252
3096.631
2783.7315
2282.6671
1623.5036
846.4689
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
961.54
1861.1845
2631.9214
3216.1311
3570.5817
3670.2578
3510.6292
3108.0961
2498.5286
1734.0117
878.0958
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
405.4979
706.702
892.6072
965.2066
937.8543
832.5033
676.232
497.5217
322.7455
173.277
63.5176
0.01
0.01
0.8996
45.6746
101.7233
155.0046
193.8111
210.3366
201.5119
169.0463
118.7274
59.1359
0.01
0.01
0.01
0.01
0.01
0.01
0.01
15.6315
48.1937
66.6588
65.6368
42.9509
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
48.4961
77.836
85.978
74.3293
47.4611
12.3066
0.01
0.01
0.01
0.01
0.01
0.01
46.4355
93.8028
133.5265
158.052
162.3651
145.1726
109.5351
62.8064
15.8334
0.01
0.01
0.01
69.9457
182.6891
331.3279
501.6637
673.1163
820.6356
917.4576
938.4136
863.4089
680.6349
389.0859
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
818.8391
1614.7936
2323.6803
2886.8977
3256.7479
3400.7529
3304.5625
2973.1906
2430.4909
1716.965
886.1561
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
774.1768
1484.7392
2087.4989
2545.7309
2831.9536
2929.1833
2831.682
2545.2124
2086.8002
1483.9974
773.6287
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
877.1272
1697.5591
2400.2073
2932.5803
3255.333
3345.7481
3199.7924
2832.5096
2276.6766
1579.8254
799.9062
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
368.67
642.4273
811.3097
877.173
852.1951
756.3595
614.2946
451.8889
293.1019
157.3399
57.668
0.01
0.01
0.81732
41.4448
92.2887
140.6077
175.7844
190.7453
182.7164
153.2571
107.6228
53.5977
0.01
0.01
0.01
0.01
0.01
0.01
0.01
14.1518
43.6234
60.3283
59.3947
38.8609
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
43.7873
70.2674
77.606
67.0817
42.8273
11.1041
0.01
0.01
0.01
0.01
0.01
0.01
41.8515
84.529
120.3068
142.3824
146.2457
130.7403
98.6309
56.5459
14.2537
0.01
0.01
0.01
62.9253
164.3259
297.9774
451.0978
605.1751
737.6904
824.5987
843.3033
775.7804
611.4618
349.4892
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
733.8936
1447.0465
2081.9625
2586.1813
2917.042
3045.5413
2958.9267
2661.7896
2175.5828
1536.6455
792.9635
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
691.1932
1325.3732
1863.1298
2271.7374
2526.7396
2613.0609
2525.6665
2269.7813
1860.6695
1322.9696
689.5691
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
779.9939
1509.3149
2133.6841
2606.4997
2892.8738
2972.7167
2842.5505
2515.8446
2021.8071
1402.7277
710.1162
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
326.4956
568.8358
718.2464
776.4184
754.1771
669.2468
543.4485
399.7027
259.2078
139.1211
50.9822
0.01
0.01
0.72332
36.6141
81.5159
124.1717
155.2085
168.388
161.2712
135.2454
94.9575
47.2822
0.01
0.01
0.01
0.01
0.01
0.01
0.01
12.4671
38.4206
53.123
52.2913
34.2074
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
38.4437
61.6799
68.1087
58.8615
37.5725
9.7407
0.01
0.01
0.01
0.01
0.01
0.01
36.6607
74.0295
105.3425
124.6481
128.0055
114.4121
86.2965
49.4654
12.4675
0.01
0.01
0.01
54.9925
143.5796
260.3057
393.99
528.4574
644.047
719.7811
735.963
676.9013
533.421
304.8241
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
638.3049
1258.3136
1810.0511
2247.9588
2535.0316
2646.1618
2570.3791
2311.7859
1889.1234
1334.0409
688.271
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
598.1858
1146.7862
1611.7407
1964.7981
2184.8816
2259.0425
2183.0225
1961.4327
1607.5545
1142.7555
595.5091
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
671.5488
1299.1819
1836.2173
2242.6183
2488.4607
2556.5734
2444.0846
2162.6936
1737.6164
1205.287
610.0277
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
279.5864
486.995
614.7667
664.4039
645.2217
572.4284
464.7212
341.72
221.5547
118.8849
43.5571
0.01
0.01
0.61898
31.2526
69.561
105.9352
132.3818
143.5887
137.4873
115.2724
80.9153
40.2813
0.01
0.01
0.01
0.01
0.01
0.01
0.01
10.6017
32.6608
45.1474
44.4297
29.058
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
32.5427
52.198
57.6238
49.7877
31.773
8.2362
0.01
0.01
0.01
0.01
0.01
0.01
30.9384
62.4565
88.8506
105.1062
107.909
96.4247
72.7107
41.6677
10.5005
0.01
0.01
0.01
46.2622
120.7513
218.859
331.1685
444.0758
541.0633
604.5251
617.9495
568.2054
447.6445
255.7384
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
533.4592
1051.3322
1511.8895
1877.1353
2116.257
2208.4064
2144.5545
1928.2556
1575.267
1112.0893
573.597
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
496.5032
951.5679
1336.9774
1629.3643
1811.3373
1872.2625
1808.7193
1624.6385
1331.126
945.9686
492.8128
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
553.3647
1070.2076
1512.1207
1846.2134
2047.9587
2103.3534
2010.1734
1778.1782
1428.2259
990.3667
501.0925
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
228.6225
398.0915
502.3715
542.7539
526.9091
467.3085
379.2543
278.7816
180.6885
96.9247
35.5006
0.01
0.01
0.50581
25.438
56.5974
86.1624
107.6355
116.7071
111.7096
93.6278
65.6997
32.6963
0.01
0.01
0.01
0.01
0.01
0.01
0.01
8.5826
26.4274
36.5172
35.924
23.4873
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
26.1698
41.9593
46.3033
39.992
25.5128
6.6124
0.01
0.01
0.01
0.01
0.01
0.01
24.7675
49.9778
71.0703
84.0401
86.2478
77.0391
58.0705
33.2659
8.3814
0.01
0.01
0.01
36.8612
96.1719
174.2384
263.5443
353.2542
430.2331
480.502
490.9743
451.2693
355.376
202.9441
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
420.8772
829.1039
1191.8018
1479.0887
1666.7914
1738.6235
1687.6285
1516.7608
1238.5653
874.0098
450.6045
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
387.6202
742.5496
1042.8246
1270.3008
1411.5242
1458.33
1408.1852
1264.283
1035.3929
735.4629
382.9696
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
427.1555
825.7127
1166.0947
1423.0338
1577.7562
1619.6296
1547.1096
1367.8748
1098.1227
761.0837
384.8902
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
174.3432
303.4149
382.6908
413.2328
400.9552
355.4115
288.2875
211.8003
137.2021
73.559
26.9293
0.01
0.01
0.38545
19.2546
42.8132
65.1402
81.3282
88.1332
84.312
70.6255
49.5315
24.6372
0.01
0.01
0.01
0.01
0.01
0.01
0.01
6.4393
19.8109
27.3576
26.8973
17.5761
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
19.4176
31.1122
34.3115
29.6164
18.8828
4.8929
0.01
0.01
0.01
0.01
0.01
0.01
18.2375
36.7746
52.2595
61.7554
63.3358
56.5364
42.5884
24.3818
6.141
0.01
0.01
0.01
26.9258
70.1978
127.0911
192.0982
257.3096
313.1634
349.5106
356.8789
327.7888
257.9539
147.2066
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
302.1916
594.8516
854.4301
1059.5916
1193.1532
1243.6263
1206.2278
1083.2692
883.9015
623.2551
321.0772
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
273.1159
522.7626
733.5484
892.8148
991.2405
1023.2481
987.2289
885.5923
724.6441
514.2913
267.5725
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
294.7517
569.243
803.1575
979.2168
1084.6723
1112.4171
1061.609
937.7338
752.094
520.7632
263.1062
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
117.5356
204.3382
257.4603
277.7189
269.1865
238.3604
193.1399
141.7474
91.7261
49.1266
17.9676
0.01
0.01
0.25965
12.7921
28.4082
43.1734
53.8417
58.2812
55.6918
46.5991
32.6451
16.221
0.01
0.01
0.01
0.01
0.01
0.01
0.01
4.2027
12.9073
17.8014
17.4808
11.4102
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
12.3839
19.814
21.8222
18.8115
11.9791
3.1025
0.01
0.01
0.01
0.01
0.01
0.01
11.4433
23.0381
32.6909
38.5752
39.5055
35.2139
26.4887
15.1442
3.8116
0.01
0.01
0.01
16.6
43.2059
78.1007
117.8664
157.6335
191.5523
213.4505
217.608
199.5546
156.791
89.3344
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
179.1235
351.9726
504.667
624.728
702.2114
730.5935
707.3338
634.0676
516.4189
363.4617
186.8937
0.01
0.01
0.01
0.01
0.01
0.01
0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
154.6309
295.3744
413.614
502.3608
556.5614
573.3066
551.9354
494.0384
403.3662
285.6413
148.2751
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
158.0533
304.4979
428.5526
521.1787
575.8381
589.052
560.6924
493.9735
395.1382
272.8704
137.4867
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
59.0036
102.2782
128.476
138.1575
133.494
117.8325
95.1714
69.6191
44.8999
23.9619
8.7255
-0.01
-0.01
0.11022
6.1242
13.5714
20.5607
25.5544
27.5642
26.2441
21.8771
15.2654
7.5497
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
1.8853
5.7966
7.9671
7.7909
5.0589
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
5.1508
8.2087
8.9966
7.7139
4.8818
1.2473
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
4.4632
8.9476
12.6283
14.8157
15.0824
13.3608
9.985
5.6671
1.407
-0.01
-0.01
-0.01
6.0136
15.5676
27.9579
41.9053
55.6515
67.1433
74.275
75.1614
68.4066
53.3343
30.1468
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
53.4378
103.9692
147.5652
180.7843
201.0658
206.9453
198.1618
175.6506
141.4271
98.3773
49.9798
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
33.9231
63.7223
87.701
104.6411
113.8306
115.0706
108.6573
95.3396
76.2584
52.8686
26.8472
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
19.0826
35.3567
47.7524
55.6021
58.6726
57.1639
51.6642
43.0691
32.4718
21.0402
9.8931
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
0.01
-0.34422
-1.2253
-2.3316
-3.3677
-4.0946
-4.3644
-4.1375
-3.4791
-2.5376
-1.5104
-0.60333
0.01
0.01
-0.00095108
-0.59259
-1.4224
-2.3104
-3.0636
-3.5128
-3.5444
-3.1224
-2.2959
-1.1912
0.01
0.01
0.01
0.01
0.01
0.01
0.01
-0.41953
-1.3583
-1.9428
-1.9722
-1.3258
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
-2.1172
-3.4759
-3.9197
-3.4557
-2.2465
-0.5861
0.01
0.01
0.01
0.01
0.01
0.01
-2.5418
-5.2327
-7.5776
-9.1188
-9.5196
-8.6462
-6.6236
-3.8522
-0.97805
0.01
0.01
0.01
-4.6201
-12.2567
-22.5506
-34.6237
-47.0977
-58.1996
-65.9379
-68.3355
-63.6937
-50.8561
-29.4381
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
-72.9829
-145.5021
-211.6368
-265.7414
-302.9558
-319.6642
-313.8442
-285.274
-235.5759
-168.0939
-87.619
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
-87.2567
-168.8341
-239.4641
-294.5762
-330.5312
-344.8143
-336.1767
-304.7221
-251.9355
-180.6509
-94.9502
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
-120.145
-234.2774
-333.7204
-410.7611
-459.3239
-475.5334
-458.0933
-408.44
-330.6458
-231.0753
-117.8241
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
-59.7069
-104.7309
-133.1252
-144.8639
-141.6436
-126.5178
-103.4062
-76.5467
-49.9581
-26.9807
-9.9432
0.01
0.01
-0.13196
-7.3207
-16.4154
-25.1678
-31.657
-34.5586
-33.3013
-28.0964
-19.8437
-9.9348
0.01
0.01
0.01
0.01
0.01
0.01
0.01
-2.7382
-8.5134
-11.8445
-11.7265
-7.7112
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
-9.3743
-15.1299
-16.7989
-14.595
-9.362
-2.4509
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-9.5498
-19.377
-27.7134
-32.9609
-34.0233
-30.5676
-23.176
-13.3556
-3.3888
-0.01
-0.01
-0.01
-15.2267
-39.9431
-72.7719
-110.6903
-149.2038
-182.7383
-205.2343
-210.8811
-194.9101
-154.3487
-88.636
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-198.3852
-392.9032
-567.8095
-708.453
-802.6237
-841.6776
-821.3385
-742.1012
-609.2023
-432.1672
-223.987
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-207.211
-398.9818
-563.1961
-689.5613
-770.1392
-799.7384
-776.1752
-700.4043
-576.5156
-411.5904
-215.4105
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-257.67
-500.5537
-710.3933
-871.207
-970.6989
-1001.3741
-961.2472
-854.0656
-689.0079
-479.8795
-243.8724
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-118.2236
-206.7374
-262.0081
-284.2791
-277.1583
-246.8563
-201.1952
-148.524
-96.674
-52.0796
-19.1588
-0.01
-0.01
-0.28091
-13.9624
-31.1902
-47.6801
-59.8112
-65.1231
-62.5952
-52.6829
-37.1236
-18.554
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-5.037
-15.5648
-21.5942
-21.3306
-14.0046
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-16.5153
-26.5843
-29.4544
-25.5425
-16.3616
-4.2603
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-16.3994
-33.2205
-47.4274
-56.3051
-58.0138
-52.0259
-39.3725
-22.6455
-5.7306
-0.01
-0.01
-0.01
-25.5926
-67.0304
-121.9179
-185.1319
-249.1262
-304.607
-341.5344
-350.3486
-323.28
-255.583
-146.5286
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-320.8904
-634.5863
-915.7276
-1140.8703
-1290.6316
-1351.4647
-1316.9014
-1188.1462
-973.9739
-689.9532
-357.0867
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-324.1403
-623.3234
-878.7405
-1074.5261
-1198.5585
-1243.0445
-1204.8973
-1085.9091
-892.7148
-636.541
-332.7269
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-391.4383
-759.5509
-1076.7438
-1318.9983
-1467.9765
-1512.6724
-1450.4408
-1287.2852
-1037.3579
-721.7044
-366.3641
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-175.0059
-305.7259
-387.0713
-419.5516
-408.6337
-363.5948
-296.0464
-218.3274
-141.968
-76.4033
-28.0766
-0.01
-0.01
-0.40594
-20.3819
-45.4929
-69.481
-87.0781
-94.7233
-90.9613
-76.4854
-53.8452
-26.8844
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-7.2428
-22.3707
-31.0108
-30.6055
-20.0751
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-23.397
-37.6334
-41.6629
-36.0997
-23.1041
-6.008
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-23.0113
-46.5823
-66.4538
-78.8329
-81.1631
-72.7298
-54.9981
-31.607
-7.9893
-0.01
-0.01
-0.01
-35.5875
-93.1456
-169.2959
-256.8887
-345.4357
-422.0582
-472.8816
-484.7353
-446.9616
-353.1109
-202.2963
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-438.7421
-867.0664
-1250.3654
-1556.7423
-1759.9223
-1841.6523
-1793.3661
-1616.9602
-1324.6205
-937.7331
-485.0079
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-436.3689
-838.6253
-1181.5411
-1443.9077
-1609.5957
-1668.3233
-1616.1455
-1455.6655
-1195.9676
-852.2602
-445.2181
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-519.5299
-1007.5328
-1427.479
-1747.6609
-1943.9648
-2002.0333
-1918.5993
-1701.8359
-1370.6636
-953.0628
-483.5428
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-229.2503
-400.2807
-506.5211
-548.7397
-534.183
-475.0605
-386.6043
-284.9647
-185.2032
-99.6191
-36.5875
-0.01
-0.01
-0.52522
-26.5059
-59.1359
-90.2744
-113.0823
-122.95
-118.0085
-99.1788
-69.7861
-34.825
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-9.3438
-28.8522
-39.9779
-39.4367
-25.8545
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-29.9395
-48.1368
-53.2673
-46.1336
-29.5117
-7.6688
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-29.2896
-59.2687
-84.5166
-100.2176
-103.1355
-92.3791
-69.8262
-40.1103
-10.1324
-0.01
-0.01
-0.01
-45.0665
-117.9102
-214.2189
-324.9201
-436.7357
-533.3887
-597.3709
-612.0922
-564.1613
-445.5179
-255.1303
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-550.231
-1086.9719
-1566.8699
-1950.0377
-2203.6897
-2305.1313
-2243.8225
-2022.3243
-1656.0568
-1171.9137
-605.8955
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-542.2692
-1041.7652
-1467.2065
-1792.3491
-1997.2898
-2069.4074
-2003.9555
-1804.3112
-1481.8759
-1055.6196
-551.2526
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-640.0871
-1240.903
-1757.5122
-2150.9782
-2391.7608
-2462.3597
-2358.9334
-2091.7059
-1684.0914
-1170.5995
-593.7089
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-280.1701
-489.0305
-618.6253
-669.9698
-651.9854
-579.6367
-471.5557
-347.4695
-225.7527
-121.3904
-44.5678
-0.01
-0.01
-0.63703
-32.2456
-71.9214
-109.7588
-137.4466
-149.3936
-143.3444
-120.4341
-84.715
-42.2607
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-11.3095
-34.9155
-48.3654
-47.6961
-31.2592
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-36.0479
-57.9423
-64.0993
-55.4985
-35.4914
-9.2185
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-35.1433
-71.0956
-101.3538
-120.149
-123.6123
-110.6888
-83.6419
-48.0321
-12.1287
-0.01
-0.01
-0.01
-53.892
-140.965
-256.0353
-388.2394
-521.7021
-636.9838
-713.197
-730.5723
-673.1793
-531.4639
-304.2644
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-653.7404
-1291.1138
-1860.6509
-2315.0527
-2615.4981
-2735.1802
-2661.7378
-2398.3597
-1963.4763
-1389.0987
-717.9961
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-640.3053
-1229.797
-1731.5937
-2114.797
-2356.0183
-2440.4799
-2362.7033
-2126.79
-1746.2934
-1243.67
-649.2926
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-751.3616
-1456.2771
-2062.0571
-2523.1009
-2804.8702
-2886.9757
-2765.0571
-2451.2409
-1973.0957
-1371.1597
-695.2649
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-327.0268
-570.6884
-721.7579
-781.4838
-760.3325
-675.8068
-549.6684
-404.9351
-263.0283
-141.4013
-51.9019
-0.01
-0.01
-0.73975
-37.5178
-83.664
-127.6515
-159.8178
-173.6709
-166.6015
-139.9429
-98.4155
-49.0837
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-13.1112
-40.4726
-56.0516
-55.2639
-36.2106
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-41.6337
-66.9075
-74.0019
-64.0587
-40.9565
-10.6347
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-40.4875
-81.8917
-116.7212
-138.3381
-142.2965
-127.3933
-96.2446
-55.2574
-13.9492
-0.01
-0.01
-0.01
-61.9361
-161.9755
-294.1387
-445.9285
-599.1026
-731.3411
-818.68
-838.4575
-772.4347
-609.7025
-348.9861
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-747.7689
-1476.5313
-2127.4479
-2646.4936
-2989.3752
-3125.5621
-3041.0514
-2739.6128
-2242.4204
-1586.1384
-819.6841
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-729.0555
-1399.9937
-1970.8686
-2406.5751
-2680.5786
-2776.1593
-2687.1859
-2418.425
-1985.3853
-1413.6841
-737.9164
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-851.7395
-1650.5316
-2336.697
-2858.6323
-3177.3021
-3269.7234
-3131.0806
-2775.2269
-2233.4852
-1551.8347
-786.738
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-369.141
-644.0699
-814.4233
-881.6644
-857.653
-762.1761
-619.8096
-456.5284
-296.4895
-159.3617
-58.4835
-0.01
-0.01
-0.83188
-42.2461
-94.1934
-143.6931
-179.8713
-195.4296
-187.4427
-157.4223
-110.6889
-55.195
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-14.723
-45.4429
-62.925
-62.0304
-40.6371
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-46.6159
-74.9026
-82.8314
-71.6901
-45.8278
-11.8967
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-45.2447
-91.5003
-130.3961
-154.521
-158.9172
-142.2505
-107.4517
-61.6815
-15.5675
-0.01
-0.01
-0.01
-69.082
-180.6371
-327.9765
-497.1506
-667.8147
-815.0923
-912.2903
-934.183
-860.4879
-679.0989
-388.6467
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-830.9531
-1640.5355
-2363.3916
-2939.5538
-3319.8989
-3470.6156
-3376.262
-3041.1348
-2488.8439
-1760.1751
-909.4847
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-807.2327
-1549.8871
-2181.561
-2663.4519
-2966.2638
-3071.5775
-2972.6976
-2674.9868
-2195.6842
-1563.1964
-815.8387
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-939.7652
-1820.8494
-2577.4491
-3152.7064
-3503.6551
-3605.0519
-3451.6955
-3058.965
-2461.4836
-1710.0043
-866.8014
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-405.9019
-708.1109
-895.2777
-969.0588
-942.5354
-837.4921
-680.9622
-501.5009
-325.6509
-175.011
-64.2171
-0.01
-0.01
-0.91209
-46.3618
-103.3569
-157.6509
-197.3164
-214.3542
-205.5656
-172.6188
-121.3572
-60.5059
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-16.1213
-49.7542
-68.886
-67.8974
-44.4744
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-50.9221
-81.8116
-90.4597
-78.2819
-50.0346
-12.9864
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-49.3458
-99.782
-142.18
-168.4632
-173.2334
-155.0449
-117.1006
-67.2112
-16.9603
-0.01
-0.01
-0.01
-75.2263
-196.6791
-357.0579
-541.1629
-726.8419
-887.0228
-992.6701
-1016.3606
-936.062
-738.6469
-422.671
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-902.0865
-1780.7479
-2565.0602
-3189.9831
-3602.2758
-3765.3364
-3662.5084
-3298.5526
-2699.173
-1908.685
-986.0956
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-873.7031
-1677.3033
-2360.6153
-2881.7019
-3208.9308
-3322.4501
-3215.0978
-2892.7546
-2374.1402
-1690.0384
-881.9294
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-1014.1621
-1964.7603
-2780.8217
-3401.0583
-3779.1962
-3888.098
-3722.2522
-3298.3405
-2653.7844
-1843.3746
-934.2942
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-436.7763
-761.8826
-963.1484
-1042.3995
-1013.7489
-900.6625
-732.2393
-539.2006
-350.0898
-188.1224
-69.0195
-0.01
-0.01
-0.97922
-49.8053
-111.0217
-169.3226
-211.9001
-230.1703
-220.7074
-185.312
-130.2656
-64.9395
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-17.2861
-53.3442
-73.8481
-72.7799
-47.6668
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-54.49
-87.5342
-96.7764
-83.7385
-53.516
-13.8879
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-52.7315
-106.6168
-151.9021
-179.9624
-185.0374
-165.5908
-125.0514
-71.7663
-18.1072
-0.01
-0.01
-0.01
-80.2797
-209.869
-380.9612
-577.3271
-775.3283
-946.0892
-1058.6538
-1083.7985
-998.061
-787.4827
-450.5658
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-960.1374
-1895.1351
-2729.5291
-3394.1496
-3832.4105
-4005.4503
-3895.6392
-3508.1332
-2870.3572
-2029.5142
-1048.4058
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-927.5027
-1780.3944
-2505.4349
-3058.16
-3405.0602
-3525.1388
-3410.871
-3068.5702
-2518.1652
-1792.3707
-935.23
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-1073.8511
-2080.1773
-2943.8654
-3600.0864
-3999.9296
-4114.7569
-3938.8268
-3489.8818
-2807.5986
-1950.0115
-988.2375
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-461.3164
-804.6052
-1017.0511
-1100.6229
-1070.2605
-950.7711
-772.8971
-569.0806
-369.4516
-198.5057
-72.8211
-0.01
-0.01
-1.0323
-52.5267
-117.0765
-178.5387
-223.4108
-242.6485
-232.6486
-195.3179
-137.285
-68.4314
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-18.2002
-56.1606
-77.7394
-76.6071
-50.168
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-57.2678
-91.9875
-101.6896
-87.9809
-56.2213
-14.5881
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-55.3525
-111.9055
-159.4213
-188.8518
-194.158
-173.7354
-131.1888
-75.2808
-18.9917
-0.01
-0.01
-0.01
-84.1691
-220.0153
-399.3397
-605.1187
-812.5705
-991.4351
-1109.2845
-1135.5188
-1045.5857
-824.8981
-471.9263
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-1004.264
-1982.0381
-2854.4129
-3549.0924
-4006.9657
-4187.4751
-4072.2734
-3666.837
-2999.9141
-2120.9104
-1095.5115
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-967.8513
-1857.6655
-2613.9193
-3190.2672
-3551.8076
-3676.7042
-3557.1779
-3199.8839
-2625.6706
-1868.7092
-974.9676
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-1117.9667
-2165.4266
-3064.2156
-3746.9042
-4162.6538
-4281.7415
-4098.2785
-3630.8111
-2920.6956
-2028.3683
-1027.849
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-479.1665
-835.6592
-1056.2042
-1142.8846
-1111.2508
-987.0913
-802.3461
-590.7076
-383.4555
-206.0103
-75.5667
-0.01
-0.01
-1.0705
-54.4864
-121.4335
-185.1658
-231.6816
-251.6078
-241.2159
-202.4914
-142.3135
-70.9311
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-18.8506
-58.1628
-80.5034
-79.3234
-51.9419
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-59.2152
-95.1069
-105.1283
-90.9475
-58.1115
-15.0769
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-57.171
-115.5714
-164.6287
-195.0025
-200.4629
-179.3605
-135.4238
-77.7036
-19.6008
-0.01
-0.01
-0.01
-86.8379
-226.971
-411.927
-624.1347
-838.0285
-1022.4028
-1143.8279
-1170.7712
-1077.9468
-850.3506
-486.4428
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-1033.8264
-2040.1966
-2937.9006
-3652.5645
-4123.4098
-4308.771
-4189.8494
-3772.3624
-3085.9648
-2181.5481
-1126.7297
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-994.1638
-1907.9957
-2684.4954
-3276.1074
-3647.045
-3774.9481
-3651.8969
-3284.7912
-2695.0972
-1917.9468
-1000.5657
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-1145.8691
-2219.2718
-3140.1271
-3839.3824
-4265.0091
-4386.6301
-4198.2949
-3719.0844
-2991.4353
-2077.3087
-1052.5541
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-490.0675
-854.5941
-1080.0397
-1168.5717
-1136.1252
-1009.0962
-820.1592
-603.768
-391.8985
-210.5274
-77.2166
-0.01
-0.01
-1.0934
-55.6561
-124.0295
-189.1076
-236.5926
-256.9183
-246.2851
-206.7283
-145.2783
-72.4023
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-19.2277
-59.3215
-82.1001
-80.8894
-52.9626
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-60.3039
-96.8472
-107.0424
-92.5952
-59.159
-15.3472
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-58.1604
-117.5614
-167.4487
-198.3253
-203.8608
-182.3846
-137.6949
-78.9997
-19.9259
-0.01
-0.01
-0.01
-88.2474
-230.6353
-418.5404
-634.0992
-851.3331
-1038.5432
-1161.783
-1189.0446
-1094.6751
-863.4709
-493.9048
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-1048.3958
-2068.7672
-2978.7814
-3703.0652
-4180.0541
-4367.5788
-4246.662
-3823.1791
-3127.2612
-2210.548
-1141.6075
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-1006.0584
-1930.6554
-2716.1396
-3314.4359
-3689.391
-3818.4458
-3693.6542
-3322.0608
-2725.4381
-1939.3694
-1011.6532
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-1157.1536
-2240.932
-3170.4989
-3876.1799
-4305.511
-4427.9014
-4237.4254
-3753.4217
-3018.7916
-2096.123
-1061.9947
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-493.8615
-861.1353
-1088.212
-1177.3116
-1144.5231
-1016.4668
-826.078
-608.0724
-394.6582
-211.9914
-77.7468
-0.01
-0.01
-1.1006
-56.0188
-124.827
-190.307
-238.0726
-258.5029
-247.7827
-207.9673
-146.1363
-72.8235
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-19.3262
-59.6201
-82.5062
-81.2825
-53.2153
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-60.5183
-97.183
-107.4044
-92.9002
-59.3488
-15.3951
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-58.3066
-117.8466
-167.8405
-198.772
-204.3024
-182.7638
-137.9692
-79.1502
-19.9621
-0.01
-0.01
-0.01
-88.3773
-230.9548
-419.084
-634.8679
-852.2914
-1039.6222
-1162.8894
-1190.074
-1095.528
-864.0689
-494.2041
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-1047.761
-2067.3355
-2976.4624
-3699.8621
-4176.077
-4363.0457
-4241.8873
-3818.5501
-3123.2045
-2207.4893
-1139.9293
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-1003.3628
-1925.3157
-2708.393
-3304.6968
-3678.2316
-3806.5663
-3681.8441
-3311.1521
-2716.2533
-1932.6664
-1008.0694
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-1151.6566
-2230.0931
-3154.8904
-3856.763
-4283.5722
-4404.9571
-4215.1026
-3733.3249
-3002.3679
-2084.5383
-1056.0338
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-490.4933
-855.1881
-1080.6026
-1168.9777
-1136.3226
-1009.0962
-820.0168
-603.5583
-391.6944
-210.3812
-77.1496
-0.01
-0.01
-1.0919
-55.5692
-123.8143
-188.7466
-236.1
-256.3388
-245.6869
-206.1904
-144.8751
-72.1888
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-19.1444
-59.0542
-81.7159
-80.497
-52.6965
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-59.8551
-96.1096
-106.2088
-91.8581
-58.6779
-15.2198
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-57.6073
-116.4229
-165.7982
-196.3362
-201.7811
-180.4926
-136.2428
-78.153
-19.709
-0.01
-0.01
-0.01
-87.2257
-227.9251
-413.55
-626.4295
-840.8894
-1025.6242
-1147.1311
-1173.8444
-1080.4931
-852.1358
-487.3363
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-1031.9311
-2035.9224
-2930.9772
-3643.0017
-4111.5363
-4295.2375
-4175.5946
-3758.5424
-3073.8534
-2172.4167
-1121.7193
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-986.116
-1892.0542
-2661.3679
-3247.0312
-3613.7285
-3739.4821
-3616.6381
-3252.2235
-2667.6761
-1897.9349
-989.866
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-1129.4577
-2186.9124
-3093.5281
-3781.4134
-4199.5107
-4318.1297
-4131.6501
-3659.0855
-2942.4023
-2042.7226
-1034.7578
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-480.0119
-836.8385
-1057.3219
-1143.6908
-1111.6426
-987.0913
-802.0633
-590.2912
-383.0502
-205.72
-75.4336
-0.01
-0.01
-1.0676
-54.3138
-121.0061
-184.4491
-230.7035
-250.4572
-240.0282
-201.4233
-141.513
-70.5073
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-18.6852
-57.6321
-79.7407
-78.5442
-51.4135
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-58.3241
-93.6426
-103.4731
-89.4839
-57.1562
-14.824
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-56.0726
-113.3109
-161.3516
-191.0532
-196.3337
-175.6039
-132.5406
-76.0226
-19.1702
-0.01
-0.01
-0.01
-84.8092
-221.59
-402.0186
-608.9065
-817.2925
-996.7521
-1114.7366
-1140.5912
-1049.7884
-827.8447
-473.401
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-1001.1356
-1974.9833
-2842.9855
-3533.3087
-3987.368
-4165.1375
-4048.7452
-3644.0265
-2979.9238
-2105.8385
-1087.2417
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-954.5682
-1831.3532
-2575.7463
-3142.2755
-3496.8173
-3618.166
-3498.9817
-3146.1294
-2580.4109
-1835.6786
-957.3073
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-1090.879
-2112.0159
-2987.302
-3651.2237
-4054.5458
-4168.6785
-3988.2783
-3531.7801
-2839.7645
-1971.2824
-998.4754
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-462.5692
-806.3528
-1018.7075
-1101.8175
-1070.8412
-950.7711
-772.478
-568.4636
-368.8509
-198.0755
-72.6239
-0.01
-0.01
-1.0279
-52.2709
-116.4432
-177.4767
-221.9614
-240.9435
-230.8886
-193.7353
-136.0987
-67.8034
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-17.9552
-55.3742
-76.6092
-75.4524
-49.3851
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-55.9473
-89.8176
-99.2369
-85.8122
-54.8058
-14.2133
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-53.725
-108.5557
-154.5651
-182.9995
-188.0391
-168.1687
-126.9164
-72.7897
-18.3535
-0.01
-0.01
-0.01
-81.1629
-212.0414
-384.657
-582.5528
-781.8429
-953.4248
-1066.1757
-1090.7967
-1003.8592
-791.5479
-452.6003
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-955.8213
-1885.402
-2713.7634
-3372.3737
-3805.3727
-3974.6325
-3863.1788
-3476.663
-2842.7778
-2008.7205
-1036.9965
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-909.1768
-1744.093
-2452.7699
-2991.949
-3329.1935
-3444.3774
-3330.5813
-2994.4086
-2455.7234
-1746.8004
-910.8653
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-1036.4798
-2006.49
-2837.7524
-3468.0822
-3850.7797
-3958.771
-3787.0665
-3353.2551
-2695.943
-1871.2536
-947.7126
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-438.4183
-764.1731
-965.3193
-1043.9653
-1014.5099
-900.6625
-731.69
-538.3919
-349.3025
-187.5586
-68.761
-0.01
-0.01
-0.97342
-49.4701
-110.1917
-167.9306
-210.0004
-227.9357
-218.4007
-183.2377
-128.7108
-64.1163
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-16.9649
-52.3134
-72.3668
-71.2665
-46.6406
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-52.7593
-84.6901
-93.5616
-80.8961
-51.6607
-13.3966
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-50.5983
-102.2264
-145.5372
-172.292
-177.0175
-158.2947
-119.4518
-68.5014
-17.2708
-0.01
-0.01
-0.01
-76.3397
-199.4178
-361.7171
-547.7509
-735.0547
-896.2705
-1002.1527
-1025.183
-943.3717
-743.7717
-425.2359
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-896.6453
-1768.4778
-2545.1849
-3162.5309
-3568.19
-3726.4853
-3621.5866
-3258.8792
-2664.4045
-1882.471
-971.7122
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-850.6002
-1631.5392
-2294.2223
-2798.2317
-3113.288
-3220.6367
-3113.8791
-2799.2613
-2295.4216
-1632.5893
-851.2135
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-967.0492
-1871.865
-2647.0483
-3234.6447
-3591.1677
-3691.4514
-3530.9326
-3126.0995
-2513.0236
-1744.0871
-883.2058
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-407.9093
-710.9111
-897.9317
-970.973
-943.4659
-837.4921
-680.2907
-500.5123
-324.6885
-174.3217
-63.9011
-0.01
-0.01
-0.905
-45.952
-102.3422
-155.9492
-194.994
-211.6223
-202.7456
-170.0828
-119.4564
-59.4996
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-15.7287
-48.4941
-67.075
-66.0472
-43.2198
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-48.8063
-78.3346
-86.5296
-74.8069
-47.7665
-12.3858
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-46.7379
-94.4146
-134.3988
-159.086
-163.4289
-146.1253
-110.2549
-63.2197
-15.9377
-0.01
-0.01
-0.01
-70.4095
-183.9023
-333.5315
-505.0052
-677.6066
-826.1181
-923.596
-944.7016
-869.203
-685.2092
-391.7047
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-824.4658
-1625.9062
-2339.6949
-2906.8235
-3279.2596
-3424.2947
-3327.4722
-2993.8334
-2447.3906
-1728.921
-892.3359
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-779.6879
-1495.324
-2102.4027
-2563.933
-2852.232
-2950.1886
-2852.0179
-2563.5177
-2101.8306
-1494.7017
-779.2172
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-883.5941
-1710.0933
-2417.9554
-2954.2967
-3279.4746
-3370.5964
-3223.5913
-2853.6075
-2293.6591
-1591.627
-805.8904
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-371.4847
-647.3392
-817.5219
-883.8992
-858.7393
-762.1761
-619.0256
-455.3741
-295.3658
-158.5569
-58.1146
-0.01
-0.01
-0.8236
-41.7676
-93.0087
-141.7063
-177.1599
-192.24
-184.1503
-154.4615
-108.4697
-54.02
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-14.2646
-43.9717
-60.8106
-59.8702
-39.1724
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-44.1456
-70.8432
-78.2429
-67.633
-43.1797
-11.1955
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-42.1999
-85.2338
-121.3113
-143.573
-147.4704
-131.8367
-99.4592
-57.0214
-14.3737
-0.01
-0.01
-0.01
-63.4583
-165.7199
-300.509
-454.9359
-610.3315
-743.985
-831.645
-850.5199
-782.4287
-616.7094
-352.4929
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-740.3296
-1459.755
-2100.2735
-2608.9598
-2942.7717
-3072.4432
-2985.1012
-2685.3695
-2194.8834
-1550.2975
-800.0185
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-697.4682
-1337.423
-1880.0931
-2292.4509
-2549.8115
-2636.9554
-2548.7952
-2290.5968
-1877.7578
-1335.1372
-695.9203
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-787.3248
-1523.5211
-2153.7962
-2631.1041
-2920.221
-3000.8593
-2869.4999
-2539.7311
-2041.0308
-1416.0844
-716.8876
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-329.6728
-574.3793
-725.2561
-784.0069
-761.5589
-675.8068
-548.7832
-403.632
-261.7596
-140.4927
-51.4855
-0.01
-0.01
-0.7304
-36.9777
-82.3265
-125.4084
-156.7566
-170.0699
-162.8844
-136.6002
-95.9101
-47.7572
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-12.5937
-38.8117
-53.6645
-52.8251
-34.5571
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-38.8448
-62.3245
-68.8216
-59.4784
-37.9669
-9.843
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-37.0501
-74.8169
-106.4648
-125.978
-129.3732
-115.6364
-87.2212
-49.9962
-12.6014
-0.01
-0.01
-0.01
-55.587
-145.1343
-263.1285
-398.2689
-534.2052
-651.0625
-727.6332
-744.0035
-684.3075
-539.266
-308.1691
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-645.4569
-1272.4338
-1830.3929
-2273.2597
-2563.6062
-2676.0336
-2599.4387
-2337.9611
-1910.545
-1349.1907
-696.0989
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-605.1336
-1160.1261
-1630.5175
-1987.7225
-2210.4124
-2285.4798
-2208.6087
-1984.4564
-1626.4528
-1156.2099
-602.531
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-679.6373
-1314.854
-1858.4015
-2269.7538
-2518.6168
-2587.6023
-2473.7935
-2189.0223
-1758.8025
-1220.005
-617.4883
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-283.0799
-493.0896
-622.4724
-672.7445
-653.3341
-579.6367
-470.5822
-346.0363
-224.3575
-120.3912
-44.1098
-0.01
-0.01
-0.62675
-31.6516
-70.4505
-107.292
-134.0801
-145.4335
-139.2565
-116.758
-81.9597
-40.802
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-10.7403
-33.0889
-45.7402
-45.014
-29.4407
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-32.9809
-52.9021
-58.4023
-50.4614
-32.2036
-8.3479
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-31.363
-63.3152
-90.0743
-106.556
-109.4
-97.7591
-73.7185
-42.2461
-10.6464
-0.01
-0.01
-0.01
-46.9096
-122.444
-221.9321
-335.8262
-450.3317
-548.6979
-613.069
-626.6973
-576.2621
-454.002
-259.3763
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-541.2235
-1066.6591
-1533.9671
-1904.5916
-2147.262
-2240.8148
-2176.0779
-1956.6464
-1598.4989
-1128.5174
-582.0843
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-504.0231
-966.0045
-1357.2953
-1654.1673
-1838.9567
-1900.859
-1836.3918
-1649.5366
-1351.5603
-960.5148
-500.4035
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-562.0936
-1087.1183
-1536.0554
-1875.4865
-2080.4864
-2136.8185
-2042.211
-1806.5672
-1451.0672
-1006.2327
-509.1339
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-232.3818
-404.649
-510.6614
-551.7258
-535.6345
-475.0605
-385.5567
-283.4224
-183.7017
-98.5438
-36.0945
-0.01
-0.01
-0.51416
-25.8666
-57.5529
-87.6197
-109.4592
-118.6881
-113.6092
-95.2227
-66.8208
-33.2551
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-8.7313
-26.8865
-37.1528
-36.5503
-23.8975
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-26.6387
-42.7126
-47.1362
-40.7126
-25.9734
-6.7319
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-25.2212
-50.8954
-72.3777
-85.589
-87.8403
-78.4643
-59.1468
-33.8835
-8.5372
-0.01
-0.01
-0.01
-37.5521
-97.9781
-177.5173
-268.5133
-359.9274
-438.376
-489.6138
-500.3026
-459.8596
-362.1539
-206.822
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-429.1411
-845.4153
-1215.295
-1508.3023
-1699.7772
-1773.0986
-1721.1585
-1546.9555
-1263.2706
-891.4779
-459.6281
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-395.6032
-757.8735
-1064.389
-1296.6225
-1440.8317
-1488.671
-1437.5427
-1290.6943
-1057.0668
-750.8899
-391.0191
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-436.3982
-843.6168
-1191.4327
-1454.02
-1612.1838
-1655.0455
-1581.0113
-1397.9123
-1122.2878
-777.8675
-393.396
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-178.3137
-310.3402
-391.4446
-422.7058
-410.1669
-363.5948
-294.9398
-216.6983
-140.3819
-75.2674
-27.556
-0.01
-0.01
-0.39425
-19.7066
-43.8208
-66.6768
-83.2511
-90.2216
-86.3143
-72.3065
-50.713
-25.2261
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-6.5959
-20.2942
-28.0266
-27.5566
-18.0078
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-19.9104
-31.9039
-35.1867
-30.3736
-19.3666
-5.0184
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-18.7139
-37.7376
-53.6315
-63.3807
-65.0069
-58.0316
-43.7174
-25.0296
-6.3043
-0.01
-0.01
-0.01
-27.6501
-72.0915
-130.5281
-197.3065
-264.3034
-321.6967
-359.0582
-366.6523
-336.7881
-265.0538
-151.2684
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-310.8353
-611.911
-878.9981
-1090.1389
-1227.6414
-1279.6681
-1241.278
-1114.8299
-909.7219
-641.5098
-330.5063
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-281.4462
-538.7516
-756.0465
-920.2735
-1021.8111
-1054.8937
-1017.8457
-913.1339
-747.2433
-530.3754
-275.9641
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-304.374
-587.8809
-829.5314
-1011.4666
-1120.5005
-1149.2703
-1096.8831
-968.9844
-777.2326
-538.2214
-271.9529
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-121.6598
-211.5307
-266.551
-287.5557
-278.751
-246.8563
-200.0456
-146.8316
-95.0264
-50.8996
-18.6179
-0.01
-0.01
-0.26877
-13.261
-29.4533
-44.7671
-55.8357
-60.4467
-57.7679
-48.3419
-33.8699
-16.8314
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-4.3649
-13.4078
-18.4942
-18.1634
-11.8572
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-12.8935
-20.6325
-22.727
-19.5942
-12.4792
-3.2322
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-11.9352
-24.0327
-34.1077
-40.2535
-41.2308
-36.7575
-27.6542
-15.8129
-3.9802
-0.01
-0.01
-0.01
-17.3473
-45.1594
-81.6461
-123.2383
-164.8464
-200.3521
-223.2954
-227.6848
-208.8325
-164.1099
-93.5212
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-188.0216
-369.5326
-529.9537
-656.1658
-737.7018
-767.6793
-743.396
-666.5366
-542.98
-382.2383
-196.5914
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-163.2076
-311.8165
-436.7396
-530.5784
-587.9717
-605.8178
-583.3675
-522.3108
-426.5631
-302.1491
-156.887
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
-167.9158
-323.5993
-455.5798
-554.2245
-612.5473
-626.8079
-596.8274
-525.9838
-420.8857
-290.7499
-146.546
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
-63.2216
-109.6336
-137.7719
-148.2154
-143.2727
-126.5178
-102.2304
-74.8157
-48.2729
-25.7738
-9.39
0.01
0.01
-0.11954
-6.6032
-14.6388
-22.1883
-27.5907
-29.7754
-28.3638
-23.6563
-16.5157
-8.1728
0.01
0.01
0.01
0.01
0.01
0.01
0.01
-2.0508
-6.3071
-8.6737
-8.487
-5.5147
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
-5.6698
-9.0421
-9.9178
-8.5108
-5.3909
-1.3794
0.01
0.01
0.01
0.01
0.01
0.01
-4.9637
-9.9594
-14.0694
-16.5226
-16.837
-14.9305
-11.1701
-6.347
-1.5784
0.01
0.01
0.01
-6.7731
-17.5526
-31.5602
-47.363
-62.9789
-76.082
-84.2745
-85.3955
-77.8284
-60.7661
-34.3978
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
-62.4614
-121.7751
-173.2037
-212.6568
-237.0438
-244.5373
-234.7131
-208.5569
-168.3436
-117.4036
-59.8057
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
-42.5823
-80.3395
-111.0789
-133.1687
-145.5854
-147.9362
-140.4488
-123.9327
-99.7164
-69.5608
-35.5545
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
-29.0422
-54.6445
-75.0411
-88.9646
-95.7304
-95.2751
-88.136
-75.375
-58.4546
-39.0816
-19.0337
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
-3.8864
-6.1665
-7.0147
-6.7454
-5.7364
-4.3644
-2.9525
-1.7346
-0.8392
-0.29409
-0.045758
-0.01
-0.01
-0.0084355
0.11052
0.34811
0.67248
1.0145
1.2879
1.4118
1.3325
1.0382
0.56452
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
0.25327
0.84524
1.2328
1.2727
0.86788
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
1.5964
2.6395
2.9953
2.6561
1.7358
0.45368
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
2.04
4.2185
6.133
7.408
7.7612
7.0732
5.4362
3.1711
0.80632
-0.01
-0.01
-0.01
3.8596
10.269
18.9436
29.1594
39.7621
49.2516
55.9289
58.0925
54.2645
43.419
25.1845
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
63.9649
127.7085
186.0183
233.8965
267.0121
282.1112
277.334
252.4075
208.6943
149.094
77.8076
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
78.6208
152.2628
216.1528
266.1325
298.8724
312.051
304.4869
276.2228
228.5566
164.0164
86.2738
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
110.2327
215.0829
306.5661
377.5657
422.455
437.6197
421.8137
376.3071
304.8042
213.1336
108.7348
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
55.4853
97.3703
123.8245
134.8025
131.8633
117.8325
96.3484
71.3519
46.5868
25.1701
9.2793
-0.01
-0.01
0.12265
6.8425
15.3498
23.5433
29.625
32.3524
31.1868
26.3218
18.5968
9.3135
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
2.5735
8.0052
11.1412
11.0337
7.2577
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
8.8592
14.3028
15.8849
13.8044
8.8571
2.3
-0.01
-0.01
-0.01
-0.01
-0.01
-0.01
9.034
18.355
26.2664
31.2511
32.2667
29.0142
22.0035
12.683
3.2193
0.01
0.01
0.01
14.4761
37.9814
69.2125
105.2987
141.9663
173.9108
195.3609
200.7778
185.6103
147.0144
84.4415
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
189.5033
375.3799
542.5824
677.0975
767.2355
804.7083
785.3989
709.7512
582.7455
413.4692
214.3323
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
198.7235
382.6968
540.2896
661.6139
739.0357
767.5525
745.0466
672.4123
553.5548
395.2549
206.8907
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
247.9488
481.7309
683.7672
838.6601
934.5535
964.2077
925.6859
822.5716
663.6825
462.2977
234.9663
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
114.0922
199.5348
252.9077
274.4353
267.5904
238.3604
194.2918
143.4434
93.3771
50.309
18.5096
0.01
0.01
0.27181
13.4951
30.1488
46.0926
57.8256
62.9675
60.5293
50.9493
35.9056
17.9473
0.01
0.01
0.01
0.01
0.01
0.01
0.01
4.8762
15.0688
20.9079
20.6546
13.5622
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
16.0134
25.7784
28.5639
24.7724
15.8698
4.1328
0.01
0.01
0.01
0.01
0.01
0.01
15.9168
32.2453
46.0387
54.6608
56.3241
50.5145
38.2318
21.9912
5.5656
0.01
0.01
0.01
24.8628
65.1232
118.4578
179.8911
242.0918
296.0279
331.9399
340.5315
314.2444
248.4578
142.4541
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
312.2737
617.5875
891.2579
1110.459
1256.3121
1315.6152
1282.0536
1156.7819
948.3255
671.8281
347.7288
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
315.9243
607.5609
856.571
1047.4804
1168.4612
1211.9027
1174.7814
1058.8302
870.5051
620.7412
324.4874
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
382.0491
741.3727
1051.032
1287.572
1433.0788
1476.7924
1416.1134
1256.8869
1012.9159
704.7375
357.7703
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
171.0246
298.7856
378.3033
410.0683
399.417
355.4115
289.3977
213.4347
138.7933
74.6986
27.4517
0.01
0.01
0.39718
19.9321
44.4907
67.9535
85.1677
92.6496
88.9742
74.818
52.6739
26.3009
0.01
0.01
0.01
0.01
0.01
0.01
0.01
7.0884
21.8941
30.3515
29.9561
19.6501
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
22.9155
36.8604
40.8088
35.3612
22.6325
5.8858
0.01
0.01
0.01
0.01
0.01
0.01
22.549
45.648
65.1235
77.2579
79.5448
71.2824
53.9058
30.9806
7.8315
0.01
0.01
0.01
34.8891
91.3207
165.9853
251.8747
338.7064
413.8521
463.705
475.3468
438.3214
346.2981
198.4008
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
430.5154
850.8387
1227.0079
1527.7161
1727.1692
1807.4424
1760.1155
1587.0364
1300.1525
920.444
476.0825
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
428.5436
823.6139
1160.43
1418.1559
1580.9412
1638.6774
1587.479
1429.8925
1174.8311
837.2254
437.3783
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
510.6089
990.2628
1403.0543
1717.811
1910.8209
1967.9599
1886.0038
1672.9743
1347.4595
936.9568
475.3858
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
225.4768
393.7035
498.2127
539.7543
525.4511
467.3085
380.3067
280.3308
182.1968
98.0049
35.9957
0.01
0.01
0.51693
26.0801
58.1875
88.8291
111.2749
120.9882
116.1288
97.6018
68.6783
34.2733
0.01
0.01
0.01
0.01
0.01
0.01
0.01
9.1979
28.4021
39.3552
38.8233
25.4532
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
29.4855
47.408
52.4621
45.4374
29.0671
7.5536
0.01
0.01
0.01
0.01
0.01
0.01
28.8542
58.3889
83.264
98.7347
101.612
91.0167
68.7982
39.5208
9.9838
0.01
0.01
0.01
44.4095
116.1939
211.1057
320.2056
430.4091
525.6745
588.7454
603.2684
556.0417
439.1163
251.4703
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
542.5136
1071.7506
1544.9634
1922.8176
2172.9781
2273.0573
2212.6513
1994.275
1633.1242
1155.7112
597.5319
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
534.9481
1027.7225
1447.46
1768.2646
1970.4936
2041.6872
1977.1542
1780.2179
1462.1191
1041.5679
543.9262
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
631.7637
1224.7918
1734.7289
2123.1374
2360.8514
2430.5872
2328.5425
2064.7994
1662.4617
1155.5881
586.1072
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
276.6593
482.9118
610.8968
661.6127
643.865
572.4284
465.7004
343.1616
222.9581
119.8901
44.0179
0.01
0.01
0.62933
31.8502
71.0406
108.4166
135.7684
147.5723
141.5994
118.9703
83.6869
41.7487
0.01
0.01
0.01
0.01
0.01
0.01
0.01
11.1742
34.4982
47.7882
47.1277
30.8873
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
35.6279
57.2681
63.3546
54.8547
35.0803
9.112
0.01
0.01
0.01
0.01
0.01
0.01
34.7412
70.2831
100.1971
118.7798
122.2057
109.4311
82.693
47.4881
11.9916
0.01
0.01
0.01
53.286
139.3822
253.1647
383.8929
515.87
629.8734
705.2476
722.4413
665.6981
525.5663
300.8931
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
646.6442
1277.1196
1840.5131
2290.0335
2587.2733
2705.7071
2633.0981
2372.5916
1942.4115
1374.2179
710.3158
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
633.5945
1216.9267
1713.4983
2092.7291
2331.469
2415.0874
2338.1558
2104.7257
1728.2028
1230.8051
642.5859
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
743.7565
1441.5583
2041.2456
2497.6731
2776.6436
2857.9648
2737.3115
2426.6798
1953.3541
1357.4605
688.3287
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
323.8295
565.1167
714.7215
773.8761
752.9413
669.2468
544.3405
401.0158
260.4861
140.0367
51.4018
0.01
0.01
0.73274
37.1584
82.8635
126.4319
158.293
172.0163
165.0166
138.6135
97.482
48.6188
0.01
0.01
0.01
0.01
0.01
0.01
0.01
12.9885
40.0942
55.5282
54.7487
35.8736
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
41.2538
66.2979
73.3285
63.4767
40.5849
10.5384
0.01
0.01
0.01
0.01
0.01
0.01
40.1244
81.1582
115.6772
137.1024
141.0273
126.2587
95.3886
54.7667
13.8256
0.01
0.01
0.01
61.3899
160.5492
291.5523
442.0129
593.8495
724.9377
811.5221
831.1371
765.7003
604.3945
345.9522
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
741.397
1463.9672
2109.3708
2624.0382
2964.0466
3099.1175
3015.3585
2716.4997
2223.529
1572.795
812.7983
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
723.0524
1388.4825
1954.6866
2386.8439
2658.6322
2753.4629
2665.2483
2398.7097
1969.2234
1402.1926
731.9267
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
844.9631
1637.4186
2318.1592
2835.9863
3152.1676
3243.8948
3106.3826
2753.3673
2215.918
1539.6465
780.5678
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
366.3036
639.1262
808.1811
874.9165
851.0983
756.3595
615.0863
453.0544
294.2366
158.1525
58.0405
0.01
0.01
0.82568
41.9279
93.4849
142.6138
178.5222
193.9659
186.0408
156.2466
109.8635
54.784
0.01
0.01
0.01
0.01
0.01
0.01
0.01
14.6146
45.1089
62.4632
61.5758
40.3398
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
46.2816
74.3663
82.2391
71.1782
45.5011
11.8121
0.01
0.01
0.01
0.01
0.01
0.01
44.9259
90.8564
129.4798
153.4368
157.8038
141.2553
106.7011
61.2513
15.4592
0.01
0.01
0.01
68.6037
179.388
325.7118
493.7227
663.2168
809.4887
906.0275
927.7794
854.5981
674.4575
385.9943
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
825.3977
1629.5837
2347.6374
2919.9878
3297.8338
3447.5828
3353.8885
3021.0118
2472.3998
1748.5626
903.4934
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
802.0244
1539.9018
2167.5271
2646.3435
2947.2387
3051.9063
2953.6881
2657.9065
2181.6852
1553.2449
810.6528
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
933.9156
1809.5324
2561.4538
3133.1705
3481.9772
3582.7803
3430.4034
3040.124
2446.3456
1699.5037
861.4868
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
403.4655
703.8669
889.9201
963.2685
936.9122
832.5033
676.912
498.5227
323.72
173.9749
63.8375
0.01
0.01
0.90678
46.0895
102.7507
156.7275
196.1625
213.1025
204.3671
171.6139
120.6518
60.1548
0.01
0.01
0.01
0.01
0.01
0.01
0.01
16.029
49.4695
68.4924
67.5101
44.221
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
50.6383
81.3563
89.9572
77.8476
49.7575
12.9146
0.01
0.01
0.01
0.01
0.01
0.01
49.076
99.2371
141.4048
167.5461
172.2919
154.2035
116.4662
66.8477
16.8687
0.01
0.01
0.01
74.8226
195.6253
355.1478
538.2725
722.966
882.3002
987.3934
1010.9667
931.1022
734.7393
420.4387
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
897.4282
1771.5672
2551.8573
3173.5902
3583.7942
3746.0496
3643.7788
3281.7117
2685.4146
1898.9718
981.0857
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
869.365
1668.9889
2348.9331
2867.4644
3193.1028
3306.0893
3199.2919
2878.557
2362.5073
1681.7713
877.6225
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
1009.3242
1955.4034
2767.6008
3384.916
3761.2894
3869.7063
3704.6748
3282.7914
2641.295
1834.714
929.9122
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
434.7762
758.3999
958.7532
1037.6508
1009.1387
896.5737
728.9208
536.7612
348.5087
187.2743
68.7089
0.01
0.01
0.97488
49.5828
110.5264
168.5685
210.9581
229.1488
219.7297
184.4925
129.6905
64.6534
0.01
0.01
0.01
0.01
0.01
0.01
0.01
17.211
53.1128
73.5284
72.4654
47.4612
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
54.2608
87.1667
96.3707
83.3882
53.2925
13.83
0.01
0.01
0.01
0.01
0.01
0.01
52.5145
106.1788
151.2792
179.2258
184.2814
164.9155
124.5424
71.4748
18.0338
0.01
0.01
0.01
79.9566
209.0258
379.4334
575.016
772.2304
942.3162
1054.4398
1079.4925
994.103
784.3657
448.7857
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
956.4438
1887.8586
2719.069
3381.1676
3817.7805
3990.1892
3880.8251
3494.8185
2859.4843
2021.8413
1044.4498
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
924.0978
1773.8714
2496.2737
3047
3392.6589
3512.3258
3398.498
3057.4612
2509.067
1785.9078
931.8646
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
1070.0951
2072.9163
2933.6107
3587.5716
3986.0535
4100.5119
3925.219
3477.85
2797.9391
1943.3164
984.8516
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
459.7818
801.9342
1013.682
1096.9847
1066.7303
947.6417
770.3586
567.2155
368.2434
197.858
72.584
0.01
0.01
1.029
52.3571
116.6994
177.9649
222.6943
241.872
231.9058
194.6957
136.8486
68.2144
0.01
0.01
0.01
0.01
0.01
0.01
0.01
18.1435
55.986
77.4983
76.37
50.0131
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
57.0965
91.713
101.3869
87.7195
56.0547
14.545
0.01
0.01
0.01
0.01
0.01
0.01
55.1916
111.5808
158.9598
188.3063
193.5986
173.236
130.8126
75.0654
18.9375
0.01
0.01
0.01
83.9312
219.3949
398.2164
603.4205
810.2957
988.6663
1106.1941
1132.363
1042.687
822.6169
470.6244
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
1001.5887
1976.7714
2846.8474
3539.7096
3996.3994
4176.461
4061.5897
3657.2416
2992.0842
2115.3889
1092.6669
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
965.429
1853.0285
2607.412
3182.3464
3543.0129
3667.6247
3548.4174
3192.0245
2619.2391
1864.1443
972.5924
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
1115.347
2160.3667
3057.0759
3738.1985
4153.0097
4271.8498
4088.8377
3622.471
2914.006
2023.7358
1025.5083
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
478.1194
833.8386
1053.91
1140.4097
1108.8516
984.9666
800.6244
589.4439
382.6377
205.5723
75.4065
0.01
0.01
1.0683
54.3724
121.18
184.7805
231.2011
251.0876
240.7188
202.0754
142.0221
70.7863
0.01
0.01
0.01
0.01
0.01
0.01
0.01
18.8131
58.0474
80.3443
79.1671
51.8399
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
59.1043
94.9294
104.9328
90.7789
58.0042
15.0492
0.01
0.01
0.01
0.01
0.01
0.01
57.0683
115.3647
164.3353
194.6561
200.1082
179.0442
135.1858
77.5676
19.5667
0.01
0.01
0.01
86.6886
226.5824
411.2243
623.074
836.6098
1020.6785
1141.906
1168.8116
1076.1495
848.9382
485.6379
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
1032.2082
2037.0161
2933.3393
3646.9169
4117.0604
4302.1636
4183.451
3766.6255
3081.2914
2178.2582
1125.0377
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
992.7591
1905.312
2680.7364
3271.5408
3641.9844
3769.7339
3646.8757
3280.2955
2691.4256
1915.3461
999.2153
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
1144.4238
2216.4864
3136.2058
3834.612
4259.7368
4381.235
4193.1579
3714.5572
2987.8126
2074.8061
1051.2927
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
489.5233
853.6504
1078.8538
1167.2959
1134.892
1008.0072
819.2792
603.124
391.483
210.3055
77.1357
0.01
0.01
1.0923
55.5992
123.9034
188.9165
236.3551
256.6619
246.0409
206.5246
145.136
72.3318
0.01
0.01
0.01
0.01
0.01
0.01
0.01
19.21
59.2672
82.0253
80.8163
52.915
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
60.2551
96.7693
106.957
92.5219
59.1125
15.3353
0.01
0.01
0.01
0.01
0.01
0.01
58.1176
117.4756
167.3276
198.183
203.7158
182.256
137.5986
78.945
19.9122
0.01
0.01
0.01
88.1891
230.4841
418.2686
633.6915
850.791
1037.8883
1161.0575
1188.3095
1094.0052
862.9478
493.6086
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
1047.8581
2067.719
2977.2905
3701.2347
4178.0137
4365.474
4244.6417
3821.3839
3125.8122
2209.5374
1141.0927
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
1005.6918
1929.9638
2715.1834
3313.2896
3688.1379
3817.1724
3692.4452
3320.994
2724.5797
1938.7706
1011.3471
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
1156.9035
2240.4616
3169.8529
3875.4141
4304.687
4427.0813
4236.6667
3752.7728
3018.2884
2095.7865
1061.8308
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
0.01
493.8279
861.0822
1088.1516
1177.2535
1144.4736
1016.4292
826.0525
608.0574
394.6508
211.9888
77.7463
0.01
0.01
1.1006
56.0198
124.8301
190.3129
238.0814

## Test1b
Test 1b | Sizing of one borehole based on a balanced building load for a ten year period with one peak duration (6 hours) | [21 empty] | Peak load duration of 6 hours
[23 empty] | Rb calculated by tool |  |  | Imposed Rb
Hourly Building Load |  | Month | Building monthly averaged load | Building monthly cooling peak load | Peak cooling hours | Building monthly heating peak load | Peak heating hours | Hourly Ground Load | Month | Ground monthly averaged load | Ground monthly cooling peak Load | Peak cooling hours | Ground monthly heating peak load | Peak heating hours |  | Ground yearly, monthly and hourly pulses | Parameter | Value | Units |  | Level | Sizing tool | Borehole length | Difference from mean | Rb calculated by tool | Borehole length | Difference from mean | Imposed Rb=0.13 m.k.W-1
(W) |  |  | (W) | (W) | (hr) | (W) | (hr) | (W) |  | (W) | (W) | (hr) | (W) | (hr) |  | (W) | Nb | 1 | ---- |  |  |  | (m) | % | (m.K/W) | m | % | (m.K/W)
qh |  |  | qm | qh,C | th,C | qh,H | th,H | qh |  | qm | qh,C | th,C | qh,H | th,H |  | Cooling | B | 6 | m | A | L2 | Classic ASHRAE sizing equation | 78.9 | 6.1911 | 0.122 | 81.3 | 6.6146 | 0.13
0.01 |  | 1 | 603.6193 | 0.01 | 6 | 4400.864 | 6 | 0.0071347 | 1 | 430.6625 | 0.0071347 | 6 | 3139.8715 | 6 | qh | -5585.5227 | D | 4 | m | B | L2 | Modified ASHRAE sizing equation | 79.3 | 6.7295 | 0.127 | 80 | 4.9098 | 0.13
0.01 |  | 2 | 491.6402 | 0.01 | 6 | 3706.6449 | 6 | 0.0071347 | 2 | 350.7691 | 0.0071347 | 6 | 2644.569 | 6 | qm | -817.751 | rb | 75 | mm | C | L2 | Modified + ASHRAE sizing equation -B | 77.6 | 4.4415 | 0.122 | 80 | 4.9098 | 0.13
0.01 |  | 3 | 202.2316 | -0.01 | 6 | 2208.4064 | 6 | 0.0071347 | 3 | 144.2849 | -0.012614 | 6 | 1575.6252 | 6 | qy | -119.9502 | rp,o,rp,i | 16.7, 13.7 | mm | D | L2 | Modified + ASHRAE sizing equation- F | 77.5 | 4.3069 | 0.122 | 79.9 | 4.7786 | 0.13
0.01 |  | 4 | -168.0881 | -2002.0333 | 6 | 58.6726 | 6 | 0.0071347 | 4 | -212.3621 | -2525.4407 | 6 | 41.861 | 6 |  | Heating | 2dp | 75 | mm | E | L2 | Alternative method | 73.8 | -0.67295 | 0.122 | 76.2 | -0.073437 | 0.13
0.01 |  | 5 | -430.4907 | -3605.0519 | 6 | -0.01 | 6 | 0.0071347 | 5 | -543.0373 | -4547.5491 | 6 | -0.012614 | 6 | qh | 3158.5766 | mf | 0.1 | kg.s-1.kW-1 | Est | L2 | Alternative method (short-term effects) | 69.9 | -5.9219 | 0.122 | 72.1 | -5.4501 | 0.13
0.01 |  | 6 | -685.3155 | -4386.6301 | 6 | -0.01 | 6 | 0.0071347 | 6 | -864.4829 | -5533.4615 | 6 | -0.012614 | 6 | qm | 485.0113 | ρf | 1052 | kg.m-3 | F | L2 | GHX design tool box | 74 | -0.40377 | 0.126 | 76.2 | -0.073437 | 0.13
493.8584 |  | 7 | -648.2689 | -4427.9014 | 6 | -0.01 | 6 | 352.3517 | 7 | -817.751 | -5585.5227 | 6 | -0.012614 | 6 | qy | -119.9502 | cp,f | 3795 | J.kg-1.K-1 | G | L3 | Modified Ashrae sizing equation -B (monthly) | 74.1 | -0.26918 | 0.12 | 75.9 | -0.46685 | 0.13
861.1247 |  | 8 | -477.8342 | -3726.4853 | 6 | -0.01 | 6 | 614.3841 | 8 | -602.7582 | -4700.7298 | 6 | -0.012614 | 6 |  |  | μf | 0.0052 | kg.s-1.m-1 | H | L3 | Alternative method (monthly) | 70.4 | -5.249 | 0.12 | 80 | 4.9098 | 0.13
1088.1919 |  | 9 | -186.4283 | -2136.8185 | 6 | 0.01 | 6 | 776.389 | 9 | -235.1685 | -2695.4638 | 6 | 0.0071347 | 6 |  |  | kf | 0.48 | W.m-1.K-1 | Hst | L3 | Alternative method (monthly,short-term effects) | 69.9 | -5.9219 | 0.12 | 71.3 | -6.4992 | 0.13
1177.2826 |  | 10 | 159.7481 | -7.0147 | 6 | 1967.9599 | 6 | 839.9523 | 10 | 113.9449 | -8.8486 | 6 | 1404.0745 | 6 |  |  | ρcp,g | 2073.6 | kJ.m-3.K-1 | I | L3 | EED monthly v.4.17 | 76.4 | 2.8264 | 0.127 | 76.7 | 0.58225 | 0.13
1144.4877 |  | 11 | 478.228 | 0.01 | 6 | 3746.0496 | 6 | 816.5543 | 11 | 341.1999 | 0.0071347 | 6 | 2672.6829 | 6 |  |  | ρcp,gr | 3900 | kJ.m-3.K-1 | J | L3 | GLHEpro monthly v 5.0 | 72 | -3.0956 | 0.127 | 72.64 | -4.7419 | 0.13
1016.4292 |  | 12 | 679.7949 | 0.01 | 6 | 4427.0813 | 6 | 725.1887 | 12 | 485.0113 | 0.0071347 | 6 | 3158.5766 | 6 |  |  | ρcp,pipe | 1540 | kJ.m-3.K-1 | K | L4 | EED hourly v.4.17 | 72.4 | -2.5572 | 0.127 | 72.6 | -4.7944 | 0.13
826.0423 | [7 empty] | 589.354 | [8 empty] | αg | 0.075 | m2.day-1 | L | L4 | DST (COP:Cons.) | 74.5 | 0.26918 | 0.124 | 74.8 | -1.9094 | 0.13
608.0424 | [7 empty] | 433.8182 | [8 empty] | kg | 1.8 | W.m-1.K-1 | L | L4 | DST (COP:Var.) | 73.8 | -0.67295 | 0.124 | 74.2 | -2.6962 | 0.13
394.6362 | [7 empty] | 281.5599 | [8 empty] | kgr | 1.4 | W.m-1.K-1 | X |  | Your tool
211.9783 | [7 empty] | 151.2395 | [8 empty] | Tg | 17.5 | °C
77.7415 | [7 empty] | 55.466 | [8 empty] | kp | 0.43 | W.m-1.K-1
0.01 | [7 empty] | 0.0071347 | [8 empty] | TL | 0 | °C
0.01 | [7 empty] | 0.0071347 | [8 empty] | TH | 35 | °C |  |  | Mean | 74.3 |  | 0.12347 | 76.256
1.1005 | [7 empty] | 0.78515 | [8 empty] | Rb | 0.13 | m.K.W-1 |  |  | Min | 69.9 |  | 0.12 | 71.3
56.0136 | [7 empty] | 39.9638 | [8 empty] | t | 10 | years |  |  | Max | 79.3 |  | 0.127 | 81.3
124.8147 | [7 empty] | 89.0511 | [8 empty] | Rc | 0 | m.K.W-1
190.287 | [7 empty] | 135.7635 | [8 empty] | hconv | 1000 | W.m-2.K-1
238.0461 | [7 empty] | 169.8381 | [8 empty] | q''g | 0 | W/m2
258.4726 | [7 empty] | 184.4117 | [8 empty] | Fsc | 1.04 | -----
247.7521 | [7 empty] | 176.7629 | [8 empty] | COPC | 3.825 | -----
207.9404 | [7 empty] | 148.3586 | [8 empty] | COPH | 3.49 | -----
146.1164 | [7 empty] | 104.2493
72.8132 | [7 empty] | 51.9498
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
19.3225 | [7 empty] | 13.7859
59.6084 | [7 empty] | 42.5286
82.4894 | [7 empty] | 58.8535
81.2655 | [7 empty] | 57.9802
53.2038 | [7 empty] | 37.9592
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
60.5 | [7 empty] | 43.1647
97.153 | [7 empty] | 69.3155
107.3705 | [7 empty] | 76.6053
92.8704 | [7 empty] | 66.26
59.3293 | [7 empty] | 42.3295
15.3899 | [7 empty] | 10.9802
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
58.2846 | [7 empty] | 41.5842
117.8015 | [7 empty] | 84.0475
167.7752 | [7 empty] | 119.702
198.6935 | [7 empty] | 141.7612
204.2203 | [7 empty] | 145.7045
182.6893 | [7 empty] | 130.3428
137.9121 | [7 empty] | 98.3957
79.117 | [7 empty] | 56.4474
19.9536 | [7 empty] | 14.2362
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
88.3375 | [7 empty] | 63.0259
230.8492 | [7 empty] | 164.7033
418.8898 | [7 empty] | 298.8641
634.5698 | [7 empty] | 452.7447
851.8859 | [7 empty] | 607.7925
1039.1212 | [7 empty] | 741.3787
1162.3217 | [7 empty] | 829.2783
1189.4858 | [7 empty] | 848.6589
1094.9797 | [7 empty] | 781.2319
863.6311 | [7 empty] | 616.1723
493.9506 | [7 empty] | 352.4175
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
1047.1327 | [7 empty] | 747.0947
2066.0831 | [7 empty] | 1474.0822
2974.6407 | [7 empty] | 2122.3081
3697.5748 | [7 empty] | 2638.0978
4173.4694 | [7 empty] | 2977.6329
4360.2943 | [7 empty] | 3110.9263
4239.186 | [7 empty] | 3024.5195
3816.0946 | [7 empty] | 2722.6577
3121.1768 | [7 empty] | 2226.8568
2206.0425 | [7 empty] | 1573.9386
1139.1751 | [7 empty] | 812.7639
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
1002.6117 | [7 empty] | 715.3304
1923.8624 | [7 empty] | 1372.6125
2706.3318 | [7 empty] | 1930.8786
3302.1612 | [7 empty] | 2355.9832
3675.3866 | [7 empty] | 2622.2672
3803.5984 | [7 empty] | 2713.7421
3678.9505 | [7 empty] | 2624.81
3308.5293 | [7 empty] | 2360.5266
2714.0848 | [7 empty] | 1936.4101
1931.1114 | [7 empty] | 1377.7844
1007.252 | [7 empty] | 718.6411
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
1150.6224 | [7 empty] | 820.9311
2228.0766 | [7 empty] | 1589.6592
3152.018 | [7 empty] | 2248.861
3853.2275 | [7 empty] | 2749.1508
4279.6187 | [7 empty] | 3053.3669
4400.864 | [7 empty] | 3139.8715
4211.1596 | [7 empty] | 3004.5236
3729.8093 | [7 empty] | 2661.0961
2999.5219 | [7 empty] | 2140.06
2082.5493 | [7 empty] | 1485.8303
1055.0196 | [7 empty] | 752.7217
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
489.9793 | [7 empty] | 349.5841
854.2866 | [7 empty] | 609.5053
1079.4567 | [7 empty] | 770.1568
1167.7308 | [7 empty] | 833.1374
1135.1033 | [7 empty] | 809.8588
1008.0072 | [7 empty] | 719.1799
819.1266 | [7 empty] | 584.4199
602.8994 | [7 empty] | 430.1489
391.2643 | [7 empty] | 279.1542
210.1489 | [7 empty] | 149.9343
77.0639 | [7 empty] | 54.9825
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
1.0907 | [7 empty] | 0.77817
55.5061 | [7 empty] | 39.6018
123.6729 | [7 empty] | 88.2365
188.5299 | [7 empty] | 134.5099
235.8274 | [7 empty] | 168.2551
256.0412 | [7 empty] | 182.677
245.4002 | [7 empty] | 175.0849
205.9485 | [7 empty] | 146.9375
144.7042 | [7 empty] | 103.2417
72.1032 | [7 empty] | 51.4433
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
19.1208 | [7 empty] | 13.6421
58.9809 | [7 empty] | 42.0809
81.6139 | [7 empty] | 58.2288
80.396 | [7 empty] | 57.3599
52.63 | [7 empty] | 37.5498
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
59.7744 | [7 empty] | 42.647
95.9793 | [7 empty] | 68.4781
106.0641 | [7 empty] | 75.6733
91.7324 | [7 empty] | 65.448
58.5973 | [7 empty] | 41.8072
15.1988 | [7 empty] | 10.8438
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
57.5252 | [7 empty] | 41.0423
116.2562 | [7 empty] | 82.945
165.5598 | [7 empty] | 118.1214
196.0526 | [7 empty] | 139.8771
201.4884 | [7 empty] | 143.7553
180.2296 | [7 empty] | 128.5879
136.0434 | [7 empty] | 97.0625
78.0382 | [7 empty] | 55.6777
19.6799 | [7 empty] | 14.041
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
87.0947 | [7 empty] | 62.1392
227.5813 | [7 empty] | 162.3718
412.9237 | [7 empty] | 294.6075
625.4769 | [7 empty] | 446.2572
839.6053 | [7 empty] | 599.0307
1024.0514 | [7 empty] | 730.627
1145.3647 | [7 empty] | 817.18
1172.0294 | [7 empty] | 836.2044
1078.8156 | [7 empty] | 769.6994
850.8074 | [7 empty] | 607.023
486.5734 | [7 empty] | 347.1541
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
1030.2236 | [7 empty] | 735.0306
2032.5407 | [7 empty] | 1450.1508
2926.0901 | [7 empty] | 2087.6689
3636.9041 | [7 empty] | 2594.8112
4104.6281 | [7 empty] | 2928.5169
4287.9932 | [7 empty] | 3059.3419
4168.5253 | [7 empty] | 2974.1055
3752.1552 | [7 empty] | 2677.0391
3068.6101 | [7 empty] | 2189.3522
2168.697 | [7 empty] | 1547.2939
1119.7916 | [7 empty] | 798.9344
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
984.3327 | [7 empty] | 702.2889
1888.6202 | [7 empty] | 1347.4683
2656.5205 | [7 empty] | 1895.3398
3241.0962 | [7 empty] | 2312.4153
3607.1 | [7 empty] | 2573.547
3732.5988 | [7 empty] | 2663.0863
3609.9576 | [7 empty] | 2575.5858
3246.1951 | [7 empty] | 2316.0532
2662.7141 | [7 empty] | 1899.7588
1894.3924 | [7 empty] | 1351.5865
988.0121 | [7 empty] | 704.9141
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
1127.24 | [7 empty] | 804.2486
2182.6041 | [7 empty] | 1557.2161
3087.4138 | [7 empty] | 2202.768
3773.9149 | [7 empty] | 2692.5639
4191.1559 | [7 empty] | 2990.2517
4309.5109 | [7 empty] | 3074.694
4123.3767 | [7 empty] | 2941.8934
3651.7346 | [7 empty] | 2605.3923
2936.472 | [7 empty] | 2095.076
2038.5923 | [7 empty] | 1454.4685
1032.6589 | [7 empty] | 736.7681
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
478.9944 | [7 empty] | 341.7467
835.0592 | [7 empty] | 595.7872
1055.0669 | [7 empty] | 752.7555
1141.244 | [7 empty] | 814.24
1109.2572 | [7 empty] | 791.4185
984.9666 | [7 empty] | 702.7412
800.3317 | [7 empty] | 571.0103
589.013 | [7 empty] | 420.2414
382.2182 | [7 empty] | 272.7001
205.2718 | [7 empty] | 146.4547
75.2688 | [7 empty] | 53.7018
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
1.0652 | [7 empty] | 0.76
54.1937 | [7 empty] | 38.6654
120.7377 | [7 empty] | 86.1424
184.0388 | [7 empty] | 131.3056
230.1888 | [7 empty] | 164.2321
249.8968 | [7 empty] | 178.2931
239.4895 | [7 empty] | 170.8679
200.97 | [7 empty] | 143.3855
141.1935 | [7 empty] | 100.7369
70.3477 | [7 empty] | 50.1908
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
18.642 | [7 empty] | 13.3004
57.4982 | [7 empty] | 41.0231
79.5549 | [7 empty] | 56.7598
78.3606 | [7 empty] | 55.9077
51.2931 | [7 empty] | 36.5959
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
58.182 | [7 empty] | 41.5109
93.4138 | [7 empty] | 66.6477
103.2196 | [7 empty] | 73.6438
89.2642 | [7 empty] | 63.6871
57.0155 | [7 empty] | 40.6787
14.7874 | [7 empty] | 10.5503
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
55.9316 | [7 empty] | 39.9053
113.025 | [7 empty] | 80.6396
160.9435 | [7 empty] | 114.8279
190.5686 | [7 empty] | 135.9644
195.8344 | [7 empty] | 139.7214
175.1562 | [7 empty] | 124.9682
132.2018 | [7 empty] | 94.3216
75.8277 | [7 empty] | 54.1006
19.1209 | [7 empty] | 13.6422
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
84.589 | [7 empty] | 60.3515
221.0131 | [7 empty] | 157.6856
400.9693 | [7 empty] | 286.0784
607.3131 | [7 empty] | 433.2979
815.1483 | [7 empty] | 581.5815
994.1305 | [7 empty] | 709.2793
1111.797 | [7 empty] | 793.2305
1137.5759 | [7 empty] | 811.6229
1047.006 | [7 empty] | 747.0043
825.645 | [7 empty] | 589.0705
472.1399 | [7 empty] | 336.8562
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
998.3738 | [7 empty] | 712.3068
1969.5214 | [7 empty] | 1405.1886
2835.1039 | [7 empty] | 2022.7532
3523.4892 | [7 empty] | 2513.8934
3976.2595 | [7 empty] | 2836.9301
4153.5054 | [7 empty] | 2963.3892
4037.4106 | [7 empty] | 2880.5594
3633.8001 | [7 empty] | 2592.5966
2971.5408 | [7 empty] | 2120.0965
2099.9001 | [7 empty] | 1498.2095
1084.1683 | [7 empty] | 773.5184
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
951.7784 | [7 empty] | 679.0625
1825.9883 | [7 empty] | 1302.7825
2568.183 | [7 empty] | 1832.3139
3133.0271 | [7 empty] | 2235.3116
3486.5013 | [7 empty] | 2487.5038
3607.4671 | [7 empty] | 2573.8089
3488.6112 | [7 empty] | 2489.0091
3136.783 | [7 empty] | 2237.9913
2572.7274 | [7 empty] | 1835.5562
1830.1999 | [7 empty] | 1305.7873
954.4436 | [7 empty] | 680.964
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
1087.5099 | [7 empty] | 775.9025
2105.4785 | [7 empty] | 1502.1895
2978.0344 | [7 empty] | 2124.7294
3639.8711 | [7 empty] | 2596.9281
4041.9109 | [7 empty] | 2883.7702
4155.6589 | [7 empty] | 2964.9257
3975.7944 | [7 empty] | 2836.5983
3520.7005 | [7 empty] | 2511.9038
2830.8359 | [7 empty] | 2019.7082
1965.0707 | [7 empty] | 1402.0132
995.3221 | [7 empty] | 710.1296
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
461.063 | [7 empty] | 328.9533
803.7215 | [7 empty] | 573.4288
1015.376 | [7 empty] | 724.4373
1098.2065 | [7 empty] | 783.5341
1067.3241 | [7 empty] | 761.5006
947.6417 | [7 empty] | 676.1111
769.93 | [7 empty] | 549.3197
566.5845 | [7 empty] | 404.2394
367.6291 | [7 empty] | 262.2912
197.418 | [7 empty] | 140.8512
72.3823 | [7 empty] | 51.6424
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
1.0245 | [7 empty] | 0.73092
52.0956 | [7 empty] | 37.1685
116.0517 | [7 empty] | 82.7991
176.8787 | [7 empty] | 126.1971
221.212 | [7 empty] | 157.8275
240.1283 | [7 empty] | 171.3236
230.1058 | [7 empty] | 164.1729
193.077 | [7 empty] | 137.7541
135.6353 | [7 empty] | 96.7713
67.5721 | [7 empty] | 48.2105
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
17.8929 | [7 empty] | 12.766
55.1817 | [7 empty] | 39.3704
76.3424 | [7 empty] | 54.4678
75.189 | [7 empty] | 53.6449
49.2124 | [7 empty] | 35.1114
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
55.746 | [7 empty] | 39.7729
89.4937 | [7 empty] | 63.8508
98.8784 | [7 empty] | 70.5464
85.5016 | [7 empty] | 61.0026
54.607 | [7 empty] | 38.9603
14.1617 | [7 empty] | 10.1039
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
53.527 | [7 empty] | 38.1897
108.1549 | [7 empty] | 77.1649
153.9932 | [7 empty] | 109.8691
182.3211 | [7 empty] | 130.0801
187.3406 | [7 empty] | 133.6613
167.5428 | [7 empty] | 119.5363
126.4431 | [7 empty] | 90.213
72.5178 | [7 empty] | 51.739
18.2848 | [7 empty] | 13.0456
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
80.8567 | [7 empty] | 57.6886
211.2398 | [7 empty] | 150.7126
383.2 | [7 empty] | 273.4006
580.3419 | [7 empty] | 414.0548
778.8698 | [7 empty] | 555.6979
949.7922 | [7 empty] | 677.6454
1062.1056 | [7 empty] | 757.7774
1086.6246 | [7 empty] | 775.2709
1000.0123 | [7 empty] | 713.4758
788.5087 | [7 empty] | 562.575
450.8592 | [7 empty] | 321.6732
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
952.0451 | [7 empty] | 679.2528
1877.9392 | [7 empty] | 1339.8477
2703.0015 | [7 empty] | 1928.5025
3358.9748 | [7 empty] | 2396.5179
3790.225 | [7 empty] | 2704.2007
3958.7813 | [7 empty] | 2824.46
3847.7432 | [7 empty] | 2745.238
3462.7458 | [7 empty] | 2470.555
2831.3768 | [7 empty] | 2020.0941
2000.6494 | [7 empty] | 1427.3974
1032.822 | [7 empty] | 736.8845
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
905.4211 | [7 empty] | 645.9881
1736.875 | [7 empty] | 1239.2031
2442.6004 | [7 empty] | 1742.7149
2979.5212 | [7 empty] | 2125.7902
3315.3397 | [7 empty] | 2365.3856
3430.0181 | [7 empty] | 2447.2049
3316.6711 | [7 empty] | 2366.3356
2981.8796 | [7 empty] | 2127.4729
2445.4297 | [7 empty] | 1744.7335
1739.465 | [7 empty] | 1241.051
907.0333 | [7 empty] | 647.1384
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
1032.0083 | [7 empty] | 736.3039
1997.8182 | [7 empty] | 1425.3774
2825.4661 | [7 empty] | 2015.8769
3453.04 | [7 empty] | 2463.6302
3834.048 | [7 empty] | 2735.4669
3941.5395 | [7 empty] | 2812.1585
3770.553 | [7 empty] | 2690.1653
3338.6074 | [7 empty] | 2381.9863
2684.1457 | [7 empty] | 1915.0495
1863.0506 | [7 empty] | 1329.2252
943.5508 | [7 empty] | 673.1924
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
436.4452 | [7 empty] | 311.3893
760.728 | [7 empty] | 542.7543
960.9597 | [7 empty] | 685.6131
1039.2423 | [7 empty] | 741.4651
1009.9123 | [7 empty] | 720.5391
896.5737 | [7 empty] | 639.6758
728.3625 | [7 empty] | 519.6626
535.9393 | [7 empty] | 382.375
347.7085 | [7 empty] | 248.0786
186.7012 | [7 empty] | 133.2052
68.4462 | [7 empty] | 48.8341
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.96899 | [7 empty] | 0.69134
49.2421 | [7 empty] | 35.1326
109.6828 | [7 empty] | 78.255
167.1537 | [7 empty] | 119.2586
209.0272 | [7 empty] | 149.134
226.8775 | [7 empty] | 161.8696
217.3851 | [7 empty] | 155.0971
182.3841 | [7 empty] | 130.1251
128.1102 | [7 empty] | 91.4024
63.8167 | [7 empty] | 45.5311
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
16.8846 | [7 empty] | 12.0466
52.0652 | [7 empty] | 37.1468
72.0228 | [7 empty] | 51.3859
70.9272 | [7 empty] | 50.6042
46.4182 | [7 empty] | 33.1178
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
52.5017 | [7 empty] | 37.4582
84.2759 | [7 empty] | 60.1281
93.1032 | [7 empty] | 66.4261
80.4991 | [7 empty] | 57.4335
51.4068 | [7 empty] | 36.677
13.3307 | [7 empty] | 9.511
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
50.3463 | [7 empty] | 35.9204
101.7163 | [7 empty] | 72.5712
144.8098 | [7 empty] | 103.3171
171.4295 | [7 empty] | 122.3093
176.1299 | [7 empty] | 125.6629
157.4997 | [7 empty] | 112.3709
118.8509 | [7 empty] | 84.7962
68.1562 | [7 empty] | 48.6272
17.1836 | [7 empty] | 12.26
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
75.9519 | [7 empty] | 54.1892
198.403 | [7 empty] | 141.554
359.8734 | [7 empty] | 256.7578
544.9543 | [7 empty] | 388.807
731.2958 | [7 empty] | 521.7555
891.6796 | [7 empty] | 636.184
997.0111 | [7 empty] | 711.3346
1019.9148 | [7 empty] | 727.6756
938.516 | [7 empty] | 669.6002
739.9372 | [7 empty] | 527.9208
423.0401 | [7 empty] | 301.8252
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
891.9095 | [7 empty] | 636.3481
1759.1222 | [7 empty] | 1255.0757
2531.6989 | [7 empty] | 1806.2837
3145.7469 | [7 empty] | 2244.3867
3549.2228 | [7 empty] | 2532.2535
3706.6449 | [7 empty] | 2644.569
3602.2739 | [7 empty] | 2570.1037
3241.473 | [7 empty] | 2312.6841
2650.1508 | [7 empty] | 1890.7952
1872.3843 | [7 empty] | 1335.8845
966.4973 | [7 empty] | 689.564
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
845.9329 | [7 empty] | 603.5453
1622.5727 | [7 empty] | 1157.6522
2281.594 | [7 empty] | 1627.8422
2782.8049 | [7 empty] | 1985.4396
3096.0972 | [7 empty] | 2208.9634
3202.8252 | [7 empty] | 2285.1102
3096.631 | [7 empty] | 2209.3442
2783.7315 | [7 empty] | 1986.1007
2282.6671 | [7 empty] | 1628.6078
1623.5036 | [7 empty] | 1158.3163
846.4689 | [7 empty] | 603.9277
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
961.54 | [7 empty] | 686.0271
1861.1845 | [7 empty] | 1327.8938
2631.9214 | [7 empty] | 1877.7892
3216.1311 | [7 empty] | 2294.6036
3570.5817 | [7 empty] | 2547.4924
3670.2578 | [7 empty] | 2618.608
3510.6292 | [7 empty] | 2504.7182
3108.0961 | [7 empty] | 2217.5241
2498.5286 | [7 empty] | 1782.6178
1734.0117 | [7 empty] | 1237.1602
878.0958 | [7 empty] | 626.4924
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
405.4979 | [7 empty] | 289.3094
706.702 | [7 empty] | 504.2086
892.6072 | [7 empty] | 636.8458
965.2066 | [7 empty] | 688.6431
937.8543 | [7 empty] | 669.1281
832.5033 | [7 empty] | 593.9636
676.232 | [7 empty] | 482.4693
497.5217 | [7 empty] | 354.9653
322.7455 | [7 empty] | 230.2683
173.277 | [7 empty] | 123.6274
63.5176 | [7 empty] | 45.3177
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.8996 | [7 empty] | 0.64184
45.6746 | [7 empty] | 32.5873
101.7233 | [7 empty] | 72.5762
155.0046 | [7 empty] | 110.5907
193.8111 | [7 empty] | 138.2778
210.3366 | [7 empty] | 150.0682
201.5119 | [7 empty] | 143.7721
169.0463 | [7 empty] | 120.609
118.7274 | [7 empty] | 84.7081
59.1359 | [7 empty] | 42.1915
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
15.6315 | [7 empty] | 11.1525
48.1937 | [7 empty] | 34.3846
66.6588 | [7 empty] | 47.5589
65.6368 | [7 empty] | 46.8297
42.9509 | [7 empty] | 30.644
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
48.4961 | [7 empty] | 34.6004
77.836 | [7 empty] | 55.5334
85.978 | [7 empty] | 61.3425
74.3293 | [7 empty] | 53.0315
47.4611 | [7 empty] | 33.8619
12.3066 | [7 empty] | 8.7803
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
46.4355 | [7 empty] | 33.1302
93.8028 | [7 empty] | 66.9252
133.5265 | [7 empty] | 95.2668
158.052 | [7 empty] | 112.7649
162.3651 | [7 empty] | 115.8421
145.1726 | [7 empty] | 103.5759
109.5351 | [7 empty] | 78.1497
62.8064 | [7 empty] | 44.8103
15.8334 | [7 empty] | 11.2966
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
69.9457 | [7 empty] | 49.904
182.6891 | [7 empty] | 130.3427
331.3279 | [7 empty] | 236.3915
501.6637 | [7 empty] | 357.9205
673.1163 | [7 empty] | 480.2463
820.6356 | [7 empty] | 585.4965
917.4576 | [7 empty] | 654.5757
938.4136 | [7 empty] | 669.5272
863.4089 | [7 empty] | 616.0138
680.6349 | [7 empty] | 485.6106
389.0859 | [7 empty] | 277.6
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
818.8391 | [7 empty] | 584.2147
1614.7936 | [7 empty] | 1152.102
2323.6803 | [7 empty] | 1657.8693
2886.8977 | [7 empty] | 2059.7064
3256.7479 | [7 empty] | 2323.5823
3400.7529 | [7 empty] | 2426.3251
3304.5625 | [7 empty] | 2357.6965
2973.1906 | [7 empty] | 2121.2735
2430.4909 | [7 empty] | 1734.0751
1716.965 | [7 empty] | 1224.998
886.1561 | [7 empty] | 632.2432
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
774.1768 | [7 empty] | 552.3496
1484.7392 | [7 empty] | 1059.3125
2087.4989 | [7 empty] | 1489.3617
2545.7309 | [7 empty] | 1816.2951
2831.9536 | [7 empty] | 2020.5056
2929.1833 | [7 empty] | 2089.8757
2831.682 | [7 empty] | 2020.3118
2545.2124 | [7 empty] | 1815.9252
2086.8002 | [7 empty] | 1488.8632
1483.9974 | [7 empty] | 1058.7832
773.6287 | [7 empty] | 551.9586
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
877.1272 | [7 empty] | 625.8013
1697.5591 | [7 empty] | 1211.1525
2400.2073 | [7 empty] | 1712.4688
2932.5803 | [7 empty] | 2092.2994
3255.333 | [7 empty] | 2322.5728
3345.7481 | [7 empty] | 2387.081
3199.7924 | [7 empty] | 2282.9464
2832.5096 | [7 empty] | 2020.9022
2276.6766 | [7 empty] | 1624.3337
1579.8254 | [7 empty] | 1127.1534
799.9062 | [7 empty] | 570.7067
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
368.67 | [7 empty] | 263.0339
642.4273 | [7 empty] | 458.3507
811.3097 | [7 empty] | 578.8428
877.173 | [7 empty] | 625.8341
852.1951 | [7 empty] | 608.0131
756.3595 | [7 empty] | 539.6376
614.2946 | [7 empty] | 438.279
451.8889 | [7 empty] | 322.4078
293.1019 | [7 empty] | 209.1186
157.3399 | [7 empty] | 112.2568
57.668 | [7 empty] | 41.1442
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.81732 | [7 empty] | 0.58313
41.4448 | [7 empty] | 29.5695
92.2887 | [7 empty] | 65.845
140.6077 | [7 empty] | 100.3189
175.7844 | [7 empty] | 125.4164
190.7453 | [7 empty] | 136.0905
182.7164 | [7 empty] | 130.3621
153.2571 | [7 empty] | 109.3439
107.6228 | [7 empty] | 76.7853
53.5977 | [7 empty] | 38.2402
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
14.1518 | [7 empty] | 10.0968
43.6234 | [7 empty] | 31.1239
60.3283 | [7 empty] | 43.0422
59.3947 | [7 empty] | 42.3761
38.8609 | [7 empty] | 27.7259
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
43.7873 | [7 empty] | 31.2408
70.2674 | [7 empty] | 50.1335
77.606 | [7 empty] | 55.3694
67.0817 | [7 empty] | 47.8606
42.8273 | [7 empty] | 30.5559
11.1041 | [7 empty] | 7.9224
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
41.8515 | [7 empty] | 29.8597
84.529 | [7 empty] | 60.3087
120.3068 | [7 empty] | 85.8349
142.3824 | [7 empty] | 101.5851
146.2457 | [7 empty] | 104.3415
130.7403 | [7 empty] | 93.2789
98.6309 | [7 empty] | 70.3699
56.5459 | [7 empty] | 40.3436
14.2537 | [7 empty] | 10.1696
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
62.9253 | [7 empty] | 44.8951
164.3259 | [7 empty] | 117.2411
297.9774 | [7 empty] | 212.5971
451.0978 | [7 empty] | 321.8434
605.1751 | [7 empty] | 431.7725
737.6904 | [7 empty] | 526.3178
824.5987 | [7 empty] | 588.324
843.3033 | [7 empty] | 601.6691
775.7804 | [7 empty] | 553.4938
611.4618 | [7 empty] | 436.2578
349.4892 | [7 empty] | 249.349
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
733.8936 | [7 empty] | 523.6089
1447.0465 | [7 empty] | 1032.42
2081.9625 | [7 empty] | 1485.4117
2586.1813 | [7 empty] | 1845.1551
2917.042 | [7 empty] | 2081.2133
3045.5413 | [7 empty] | 2172.8934
2958.9267 | [7 empty] | 2111.0967
2661.7896 | [7 empty] | 1899.0991
2175.5828 | [7 empty] | 1552.2066
1536.6455 | [7 empty] | 1096.3459
792.9635 | [7 empty] | 565.7533
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
691.1932 | [7 empty] | 493.1436
1325.3732 | [7 empty] | 945.6101
1863.1298 | [7 empty] | 1329.2817
2271.7374 | [7 empty] | 1620.8098
2526.7396 | [7 empty] | 1802.7455
2613.0609 | [7 empty] | 1864.3328
2525.6665 | [7 empty] | 1801.9798
2269.7813 | [7 empty] | 1619.4142
1860.6695 | [7 empty] | 1327.5264
1322.9696 | [7 empty] | 943.8952
689.5691 | [7 empty] | 491.9848
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
779.9939 | [7 empty] | 556.4999
1509.3149 | [7 empty] | 1076.8464
2133.6841 | [7 empty] | 1522.3133
2606.4997 | [7 empty] | 1859.6516
2892.8738 | [7 empty] | 2063.9701
2972.7167 | [7 empty] | 2120.9354
2842.5505 | [7 empty] | 2028.0661
2515.8446 | [7 empty] | 1794.9722
2021.8071 | [7 empty] | 1442.4927
1402.7277 | [7 empty] | 1000.8
710.1162 | [7 empty] | 506.6445
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
326.4956 | [7 empty] | 232.9439
568.8358 | [7 empty] | 405.8456
718.2464 | [7 empty] | 512.4451
776.4184 | [7 empty] | 553.9489
754.1771 | [7 empty] | 538.0805
669.2468 | [7 empty] | 477.4855
543.4485 | [7 empty] | 387.7326
399.7027 | [7 empty] | 285.1747
259.2078 | [7 empty] | 184.9362
139.1211 | [7 empty] | 99.2583
50.9822 | [7 empty] | 36.3741
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.72332 | [7 empty] | 0.51607
36.6141 | [7 empty] | 26.123
81.5159 | [7 empty] | 58.1589
124.1717 | [7 empty] | 88.5925
155.2085 | [7 empty] | 110.7361
168.388 | [7 empty] | 120.1393
161.2712 | [7 empty] | 115.0617
135.2454 | [7 empty] | 96.4931
94.9575 | [7 empty] | 67.7491
47.2822 | [7 empty] | 33.7343
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
12.4671 | [7 empty] | 8.8948
38.4206 | [7 empty] | 27.4118
53.123 | [7 empty] | 37.9015
52.2913 | [7 empty] | 37.3081
34.2074 | [7 empty] | 24.4058
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
38.4437 | [7 empty] | 27.4283
61.6799 | [7 empty] | 44.0066
68.1087 | [7 empty] | 48.5933
58.8615 | [7 empty] | 41.9957
37.5725 | [7 empty] | 26.8068
9.7407 | [7 empty] | 6.9497
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
36.6607 | [7 empty] | 26.1562
74.0295 | [7 empty] | 52.8176
105.3425 | [7 empty] | 75.1584
124.6481 | [7 empty] | 88.9323
128.0055 | [7 empty] | 91.3277
114.4121 | [7 empty] | 81.6293
86.2965 | [7 empty] | 61.5697
49.4654 | [7 empty] | 35.2919
12.4675 | [7 empty] | 8.8951
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
54.9925 | [7 empty] | 39.2353
143.5796 | [7 empty] | 102.4393
260.3057 | [7 empty] | 185.7195
393.99 | [7 empty] | 281.0989
528.4574 | [7 empty] | 377.0369
644.047 | [7 empty] | 459.5063
719.7811 | [7 empty] | 513.5401
735.963 | [7 empty] | 525.0853
676.9013 | [7 empty] | 482.9467
533.421 | [7 empty] | 380.5783
304.8241 | [7 empty] | 217.482
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
638.3049 | [7 empty] | 455.4095
1258.3136 | [7 empty] | 897.7653
1810.0511 | [7 empty] | 1291.4118
2247.9588 | [7 empty] | 1603.8445
2535.0316 | [7 empty] | 1808.6615
2646.1618 | [7 empty] | 1887.9493
2570.3791 | [7 empty] | 1833.8808
2311.7859 | [7 empty] | 1649.3831
1889.1234 | [7 empty] | 1347.8273
1334.0409 | [7 empty] | 951.7942
688.271 | [7 empty] | 491.0587
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
598.1858 | [7 empty] | 426.7858
1146.7862 | [7 empty] | 818.1941
1611.7407 | [7 empty] | 1149.9239
1964.7981 | [7 empty] | 1401.8187
2184.8816 | [7 empty] | 1558.841
2259.0425 | [7 empty] | 1611.7524
2183.0225 | [7 empty] | 1557.5146
1961.4327 | [7 empty] | 1399.4176
1607.5545 | [7 empty] | 1146.9372
1142.7555 | [7 empty] | 815.3184
595.5091 | [7 empty] | 424.8761
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
671.5488 | [7 empty] | 479.1279
1299.1819 | [7 empty] | 926.9235
1836.2173 | [7 empty] | 1310.0805
2242.6183 | [7 empty] | 1600.0343
2488.4607 | [7 empty] | 1775.4347
2556.5734 | [7 empty] | 1824.0309
2444.0846 | [7 empty] | 1743.7738
2162.6936 | [7 empty] | 1543.0106
1737.6164 | [7 empty] | 1239.732
1205.287 | [7 empty] | 859.9325
610.0277 | [7 empty] | 435.2347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
279.5864 | [7 empty] | 199.4757
486.995 | [7 empty] | 347.4549
614.7667 | [7 empty] | 438.6158
664.4039 | [7 empty] | 474.0303
645.2217 | [7 empty] | 460.3444
572.4284 | [7 empty] | 408.4088
464.7212 | [7 empty] | 331.5633
341.72 | [7 empty] | 243.8059
221.5547 | [7 empty] | 158.0719
118.8849 | [7 empty] | 84.8205
43.5571 | [7 empty] | 31.0766
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.61898 | [7 empty] | 0.44162
31.2526 | [7 empty] | 22.2977
69.561 | [7 empty] | 49.6295
105.9352 | [7 empty] | 75.5812
132.3818 | [7 empty] | 94.4501
143.5887 | [7 empty] | 102.4458
137.4873 | [7 empty] | 98.0926
115.2724 | [7 empty] | 82.243
80.9153 | [7 empty] | 57.7304
40.2813 | [7 empty] | 28.7394
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
10.6017 | [7 empty] | 7.5639
32.6608 | [7 empty] | 23.3024
45.1474 | [7 empty] | 32.2112
44.4297 | [7 empty] | 31.6991
29.058 | [7 empty] | 20.7319
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
32.5427 | [7 empty] | 23.2181
52.198 | [7 empty] | 37.2416
57.6238 | [7 empty] | 41.1127
49.7877 | [7 empty] | 35.5219
31.773 | [7 empty] | 22.669
8.2362 | [7 empty] | 5.8763
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
30.9384 | [7 empty] | 22.0735
62.4565 | [7 empty] | 44.5606
88.8506 | [7 empty] | 63.392
105.1062 | [7 empty] | 74.9898
107.909 | [7 empty] | 76.9895
96.4247 | [7 empty] | 68.7959
72.7107 | [7 empty] | 51.8767
41.6677 | [7 empty] | 29.7285
10.5005 | [7 empty] | 7.4918
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
46.2622 | [7 empty] | 33.0066
120.7513 | [7 empty] | 86.1521
218.859 | [7 empty] | 156.1487
331.1685 | [7 empty] | 236.2778
444.0758 | [7 empty] | 316.8335
541.0633 | [7 empty] | 386.0309
604.5251 | [7 empty] | 431.3087
617.9495 | [7 empty] | 440.8866
568.2054 | [7 empty] | 405.3958
447.6445 | [7 empty] | 319.3796
255.7384 | [7 empty] | 182.4609
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
533.4592 | [7 empty] | 380.6056
1051.3322 | [7 empty] | 750.0909
1511.8895 | [7 empty] | 1078.6834
1877.1353 | [7 empty] | 1339.2742
2116.257 | [7 empty] | 1509.8796
2208.4064 | [7 empty] | 1575.6252
2144.5545 | [7 empty] | 1530.0689
1928.2556 | [7 empty] | 1375.7468
1575.267 | [7 empty] | 1123.9011
1112.0893 | [7 empty] | 793.4391
573.597 | [7 empty] | 409.2426
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
496.5032 | [7 empty] | 354.2387
951.5679 | [7 empty] | 678.9123
1336.9774 | [7 empty] | 953.8893
1629.3643 | [7 empty] | 1162.4978
1811.3373 | [7 empty] | 1292.3295
1872.2625 | [7 empty] | 1335.7976
1808.7193 | [7 empty] | 1290.4616
1624.6385 | [7 empty] | 1159.126
1331.126 | [7 empty] | 949.7145
945.9686 | [7 empty] | 674.9174
492.8128 | [7 empty] | 351.6057
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
553.3647 | [7 empty] | 394.8075
1070.2076 | [7 empty] | 763.5578
1512.1207 | [7 empty] | 1078.8483
1846.2134 | [7 empty] | 1317.2124
2047.9587 | [7 empty] | 1461.151
2103.3534 | [7 empty] | 1500.6734
2010.1734 | [7 empty] | 1434.1925
1778.1782 | [7 empty] | 1268.6715
1428.2259 | [7 empty] | 1018.9921
990.3667 | [7 empty] | 706.594
501.0925 | [7 empty] | 357.513
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
228.6225 | [7 empty] | 163.1146
398.0915 | [7 empty] | 284.0252
502.3715 | [7 empty] | 358.4255
542.7539 | [7 empty] | 387.237
526.9091 | [7 empty] | 375.9323
467.3085 | [7 empty] | 333.4092
379.2543 | [7 empty] | 270.5855
278.7816 | [7 empty] | 198.9015
180.6885 | [7 empty] | 128.9153
96.9247 | [7 empty] | 69.1526
35.5006 | [7 empty] | 25.3285
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.50581 | [7 empty] | 0.36088
25.438 | [7 empty] | 18.1492
56.5974 | [7 empty] | 40.3804
86.1624 | [7 empty] | 61.474
107.6355 | [7 empty] | 76.7944
116.7071 | [7 empty] | 83.2667
111.7096 | [7 empty] | 79.7011
93.6278 | [7 empty] | 66.8003
65.6997 | [7 empty] | 46.8746
32.6963 | [7 empty] | 23.3277
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
8.5826 | [7 empty] | 6.1234
26.4274 | [7 empty] | 18.8551
36.5172 | [7 empty] | 26.0538
35.924 | [7 empty] | 25.6306
23.4873 | [7 empty] | 16.7574
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
26.1698 | [7 empty] | 18.6713
41.9593 | [7 empty] | 29.9366
46.3033 | [7 empty] | 33.0359
39.992 | [7 empty] | 28.5329
25.5128 | [7 empty] | 18.2026
6.6124 | [7 empty] | 4.7178
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
24.7675 | [7 empty] | 17.6708
49.9778 | [7 empty] | 35.6575
71.0703 | [7 empty] | 50.7063
84.0401 | [7 empty] | 59.9598
86.2478 | [7 empty] | 61.5349
77.0391 | [7 empty] | 54.9649
58.0705 | [7 empty] | 41.4314
33.2659 | [7 empty] | 23.7341
8.3814 | [7 empty] | 5.9799
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
36.8612 | [7 empty] | 26.2993
96.1719 | [7 empty] | 68.6155
174.2384 | [7 empty] | 124.3133
263.5443 | [7 empty] | 188.0302
353.2542 | [7 empty] | 252.0352
430.2331 | [7 empty] | 306.9571
480.502 | [7 empty] | 342.8224
490.9743 | [7 empty] | 350.294
451.2693 | [7 empty] | 321.9658
355.376 | [7 empty] | 253.5491
202.9441 | [7 empty] | 144.7939
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
420.8772 | [7 empty] | 300.282
829.1039 | [7 empty] | 591.5383
1191.8018 | [7 empty] | 850.3113
1479.0887 | [7 empty] | 1055.281
1666.7914 | [7 empty] | 1189.2007
1738.6235 | [7 empty] | 1240.4506
1687.6285 | [7 empty] | 1204.0673
1516.7608 | [7 empty] | 1082.1588
1238.5653 | [7 empty] | 883.6755
874.0098 | [7 empty] | 623.5772
450.6045 | [7 empty] | 321.4915
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
387.6202 | [7 empty] | 276.5543
742.5496 | [7 empty] | 529.7847
1042.8246 | [7 empty] | 744.021
1270.3008 | [7 empty] | 906.3177
1411.5242 | [7 empty] | 1007.076
1458.33 | [7 empty] | 1040.4704
1408.1852 | [7 empty] | 1004.6937
1264.283 | [7 empty] | 902.0243
1035.3929 | [7 empty] | 738.7187
735.4629 | [7 empty] | 524.7286
382.9696 | [7 empty] | 273.2362
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
427.1555 | [7 empty] | 304.7614
825.7127 | [7 empty] | 589.1188
1166.0947 | [7 empty] | 831.9702
1423.0338 | [7 empty] | 1015.2877
1577.7562 | [7 empty] | 1125.677
1619.6296 | [7 empty] | 1155.5523
1547.1096 | [7 empty] | 1103.8117
1367.8748 | [7 empty] | 975.9336
1098.1227 | [7 empty] | 783.4744
761.0837 | [7 empty] | 543.0081
384.8902 | [7 empty] | 274.6065
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
174.3432 | [7 empty] | 124.3881
303.4149 | [7 empty] | 216.4766
382.6908 | [7 empty] | 273.0373
413.2328 | [7 empty] | 294.828
400.9552 | [7 empty] | 286.0683
355.4115 | [7 empty] | 253.5744
288.2875 | [7 empty] | 205.6836
211.8003 | [7 empty] | 151.1125
137.2021 | [7 empty] | 97.8892
73.559 | [7 empty] | 52.4819
26.9293 | [7 empty] | 19.2131
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.38545 | [7 empty] | 0.27501
19.2546 | [7 empty] | 13.7375
42.8132 | [7 empty] | 30.5458
65.1402 | [7 empty] | 46.4754
81.3282 | [7 empty] | 58.025
88.1332 | [7 empty] | 62.8801
84.312 | [7 empty] | 60.1538
70.6255 | [7 empty] | 50.389
49.5315 | [7 empty] | 35.3391
24.6372 | [7 empty] | 17.5778
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
6.4393 | [7 empty] | 4.5942
19.8109 | [7 empty] | 14.1344
27.3576 | [7 empty] | 19.5188
26.8973 | [7 empty] | 19.1904
17.5761 | [7 empty] | 12.54
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
19.4176 | [7 empty] | 13.8538
31.1122 | [7 empty] | 22.1975
34.3115 | [7 empty] | 24.4801
29.6164 | [7 empty] | 21.1303
18.8828 | [7 empty] | 13.4723
4.8929 | [7 empty] | 3.4909
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
18.2375 | [7 empty] | 13.0119
36.7746 | [7 empty] | 26.2374
52.2595 | [7 empty] | 37.2854
61.7554 | [7 empty] | 44.0604
63.3358 | [7 empty] | 45.188
56.5364 | [7 empty] | 40.3368
42.5884 | [7 empty] | 30.3854
24.3818 | [7 empty] | 17.3956
6.141 | [7 empty] | 4.3814
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
26.9258 | [7 empty] | 19.2107
70.1978 | [7 empty] | 50.0839
127.0911 | [7 empty] | 90.6753
192.0982 | [7 empty] | 137.0558
257.3096 | [7 empty] | 183.5819
313.1634 | [7 empty] | 223.4318
349.5106 | [7 empty] | 249.3643
356.8789 | [7 empty] | 254.6214
327.7888 | [7 empty] | 233.8665
257.9539 | [7 empty] | 184.0416
147.2066 | [7 empty] | 105.0271
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
302.1916 | [7 empty] | 215.6037
594.8516 | [7 empty] | 424.407
854.4301 | [7 empty] | 609.6077
1059.5916 | [7 empty] | 755.9837
1193.1532 | [7 empty] | 851.2755
1243.6263 | [7 empty] | 887.2864
1206.2278 | [7 empty] | 860.6038
1083.2692 | [7 empty] | 772.8769
883.9015 | [7 empty] | 630.6346
623.2551 | [7 empty] | 444.672
321.0772 | [7 empty] | 229.078
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
273.1159 | [7 empty] | 194.8592
522.7626 | [7 empty] | 372.9739
733.5484 | [7 empty] | 523.3626
892.8148 | [7 empty] | 636.9939
991.2405 | [7 empty] | 707.2174
1023.2481 | [7 empty] | 730.0538
987.2289 | [7 empty] | 704.3553
885.5923 | [7 empty] | 631.8409
724.6441 | [7 empty] | 517.0097
514.2913 | [7 empty] | 366.9299
267.5725 | [7 empty] | 190.9042
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
294.7517 | [7 empty] | 210.2956
569.243 | [7 empty] | 406.1361
803.1575 | [7 empty] | 573.0264
979.2168 | [7 empty] | 698.6389
1084.6723 | [7 empty] | 773.878
1112.4171 | [7 empty] | 793.673
1061.609 | [7 empty] | 757.423
937.7338 | [7 empty] | 669.0422
752.094 | [7 empty] | 536.5943
520.7632 | [7 empty] | 371.5474
263.1062 | [7 empty] | 187.7176
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
117.5356 | [7 empty] | 83.8578
204.3382 | [7 empty] | 145.7886
257.4603 | [7 empty] | 183.6894
277.7189 | [7 empty] | 198.1433
269.1865 | [7 empty] | 192.0557
238.3604 | [7 empty] | 170.0623
193.1399 | [7 empty] | 137.7989
141.7474 | [7 empty] | 101.1321
91.7261 | [7 empty] | 65.4435
49.1266 | [7 empty] | 35.0502
17.9676 | [7 empty] | 12.8193
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.25965 | [7 empty] | 0.18525
12.7921 | [7 empty] | 9.1267
28.4082 | [7 empty] | 20.2683
43.1734 | [7 empty] | 30.8028
53.8417 | [7 empty] | 38.4143
58.2812 | [7 empty] | 41.5817
55.6918 | [7 empty] | 39.7343
46.5991 | [7 empty] | 33.2469
32.6451 | [7 empty] | 23.2912
16.221 | [7 empty] | 11.5732
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
4.2027 | [7 empty] | 2.9985
12.9073 | [7 empty] | 9.2089
17.8014 | [7 empty] | 12.7007
17.4808 | [7 empty] | 12.472
11.4102 | [7 empty] | 8.1408
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
12.3839 | [7 empty] | 8.8355
19.814 | [7 empty] | 14.1367
21.8222 | [7 empty] | 15.5694
18.8115 | [7 empty] | 13.4214
11.9791 | [7 empty] | 8.5467
3.1025 | [7 empty] | 2.2136
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
11.4433 | [7 empty] | 8.1644
23.0381 | [7 empty] | 16.4369
32.6909 | [7 empty] | 23.3238
38.5752 | [7 empty] | 27.5221
39.5055 | [7 empty] | 28.1859
35.2139 | [7 empty] | 25.1239
26.4887 | [7 empty] | 18.8988
15.1442 | [7 empty] | 10.8049
3.8116 | [7 empty] | 2.7194
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
16.6 | [7 empty] | 11.8435
43.2059 | [7 empty] | 30.826
78.1007 | [7 empty] | 55.7223
117.8664 | [7 empty] | 84.0938
157.6335 | [7 empty] | 112.4663
191.5523 | [7 empty] | 136.6663
213.4505 | [7 empty] | 152.2899
217.608 | [7 empty] | 155.2561
199.5546 | [7 empty] | 142.3757
156.791 | [7 empty] | 111.8652
89.3344 | [7 empty] | 63.7372
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
179.1235 | [7 empty] | 127.7987
351.9726 | [7 empty] | 251.1208
504.667 | [7 empty] | 360.0633
624.728 | [7 empty] | 445.7228
702.2114 | [7 empty] | 501.0047
730.5935 | [7 empty] | 521.2544
707.3338 | [7 empty] | 504.6593
634.0676 | [7 empty] | 452.3864
516.4189 | [7 empty] | 368.4479
363.4617 | [7 empty] | 259.3179
186.8937 | [7 empty] | 133.3425
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
154.6309 | [7 empty] | 110.324
295.3744 | [7 empty] | 210.7399
413.614 | [7 empty] | 295.1
502.3608 | [7 empty] | 358.4179
556.5614 | [7 empty] | 397.0882
573.3066 | [7 empty] | 409.0354
551.9354 | [7 empty] | 393.7877
494.0384 | [7 empty] | 352.4801
403.3662 | [7 empty] | 287.7885
285.6413 | [7 empty] | 203.7957
148.2751 | [7 empty] | 105.7894
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
158.0533 | [7 empty] | 112.7658
304.4979 | [7 empty] | 217.2492
428.5526 | [7 empty] | 305.7581
521.1787 | [7 empty] | 371.8438
575.8381 | [7 empty] | 410.8415
589.052 | [7 empty] | 420.2692
560.6924 | [7 empty] | 400.0356
493.9735 | [7 empty] | 352.4338
395.1382 | [7 empty] | 281.9181
272.8704 | [7 empty] | 194.684
137.4867 | [7 empty] | 98.0922
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
59.0036 | [7 empty] | 42.0971
102.2782 | [7 empty] | 72.9721
128.476 | [7 empty] | 91.6634
138.1575 | [7 empty] | 98.5708
133.494 | [7 empty] | 95.2436
117.8325 | [7 empty] | 84.0696
95.1714 | [7 empty] | 67.9016
69.6191 | [7 empty] | 49.6709
44.8999 | [7 empty] | 32.0346
23.9619 | [7 empty] | 17.096
8.7255 | [7 empty] | 6.2253
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
0.11022 | [7 empty] | 0.078638
6.1242 | [7 empty] | 4.3694
13.5714 | [7 empty] | 9.6827
20.5607 | [7 empty] | 14.6694
25.5544 | [7 empty] | 18.2322
27.5642 | [7 empty] | 19.6661
26.2441 | [7 empty] | 18.7243
21.8771 | [7 empty] | 15.6086
15.2654 | [7 empty] | 10.8913
7.5497 | [7 empty] | 5.3865
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
1.8853 | [7 empty] | 1.3451
5.7966 | [7 empty] | 4.1357
7.9671 | [7 empty] | 5.6843
7.7909 | [7 empty] | 5.5585
5.0589 | [7 empty] | 3.6094
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
5.1508 | [7 empty] | 3.6749
8.2087 | [7 empty] | 5.8566
8.9966 | [7 empty] | 6.4188
7.7139 | [7 empty] | 5.5036
4.8818 | [7 empty] | 3.483
1.2473 | [7 empty] | 0.88994
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
4.4632 | [7 empty] | 3.1843
8.9476 | [7 empty] | 6.3839
12.6283 | [7 empty] | 9.0099
14.8157 | [7 empty] | 10.5705
15.0824 | [7 empty] | 10.7608
13.3608 | [7 empty] | 9.5325
9.985 | [7 empty] | 7.124
5.6671 | [7 empty] | 4.0433
1.407 | [7 empty] | 1.0039
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
6.0136 | [7 empty] | 4.2905
15.5676 | [7 empty] | 11.1069
27.9579 | [7 empty] | 19.947
41.9053 | [7 empty] | 29.898
55.6515 | [7 empty] | 39.7055
67.1433 | [7 empty] | 47.9045
74.275 | [7 empty] | 52.9928
75.1614 | [7 empty] | 53.6252
68.4066 | [7 empty] | 48.8058
53.3343 | [7 empty] | 38.0522
30.1468 | [7 empty] | 21.5088
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
53.4378 | [7 empty] | 38.1261
103.9692 | [7 empty] | 74.1786
147.5652 | [7 empty] | 105.2829
180.7843 | [7 empty] | 128.9836
201.0658 | [7 empty] | 143.4538
206.9453 | [7 empty] | 147.6487
198.1618 | [7 empty] | 141.3819
175.6506 | [7 empty] | 125.3209
141.4271 | [7 empty] | 100.9036
98.3773 | [7 empty] | 70.189
49.9798 | [7 empty] | 35.659
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
33.9231 | [7 empty] | 24.203
63.7223 | [7 empty] | 45.4637
87.701 | [7 empty] | 62.5718
104.6411 | [7 empty] | 74.658
113.8306 | [7 empty] | 81.2144
115.0706 | [7 empty] | 82.0991
108.6573 | [7 empty] | 77.5234
95.3396 | [7 empty] | 68.0217
76.2584 | [7 empty] | 54.4079
52.8686 | [7 empty] | 37.72
26.8472 | [7 empty] | 19.1546
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
19.0826 | [7 empty] | 13.6148
35.3567 | [7 empty] | 25.2259
47.7524 | [7 empty] | 34.0698
55.6021 | [7 empty] | 39.6703
58.6726 | [7 empty] | 41.861
57.1639 | [7 empty] | 40.7845
51.6642 | [7 empty] | 36.8607
43.0691 | [7 empty] | 30.7284
32.4718 | [7 empty] | 23.1675
21.0402 | [7 empty] | 15.0115
9.8931 | [7 empty] | 7.0584
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
0.01 | [7 empty] | 0.0071347
-0.34422 | [7 empty] | -0.43421
-1.2253 | [7 empty] | -1.5456
-2.3316 | [7 empty] | -2.9411
-3.3677 | [7 empty] | -4.2482
-4.0946 | [7 empty] | -5.165
-4.3644 | [7 empty] | -5.5054
-4.1375 | [7 empty] | -5.2192
-3.4791 | [7 empty] | -4.3887
-2.5376 | [7 empty] | -3.201
-1.5104 | [7 empty] | -1.9053
-0.60333 | [7 empty] | -0.76106
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
-0.00095108 | [7 empty] | -0.0011997
-0.59259 | [7 empty] | -0.74752
-1.4224 | [7 empty] | -1.7943
-2.3104 | [7 empty] | -2.9144
-3.0636 | [7 empty] | -3.8645
-3.5128 | [7 empty] | -4.4311
-3.5444 | [7 empty] | -4.471
-3.1224 | [7 empty] | -3.9387
-2.2959 | [7 empty] | -2.8961
-1.1912 | [7 empty] | -1.5027
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
-0.41953 | [7 empty] | -0.52921
-1.3583 | [7 empty] | -1.7134
-1.9428 | [7 empty] | -2.4508
-1.9722 | [7 empty] | -2.4878
-1.3258 | [7 empty] | -1.6724
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
-2.1172 | [7 empty] | -2.6707
-3.4759 | [7 empty] | -4.3846
-3.9197 | [7 empty] | -4.9444
-3.4557 | [7 empty] | -4.3591
-2.2465 | [7 empty] | -2.8338
-0.5861 | [7 empty] | -0.73933
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
-2.5418 | [7 empty] | -3.2063
-5.2327 | [7 empty] | -6.6007
-7.5776 | [7 empty] | -9.5586
-9.1188 | [7 empty] | -11.5028
-9.5196 | [7 empty] | -12.0083
-8.6462 | [7 empty] | -10.9066
-6.6236 | [7 empty] | -8.3553
-3.8522 | [7 empty] | -4.8594
-0.97805 | [7 empty] | -1.2338
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
-4.6201 | [7 empty] | -5.828
-12.2567 | [7 empty] | -15.4611
-22.5506 | [7 empty] | -28.4462
-34.6237 | [7 empty] | -43.6756
-47.0977 | [7 empty] | -59.4108
-58.1996 | [7 empty] | -73.4152
-65.9379 | [7 empty] | -83.1765
-68.3355 | [7 empty] | -86.201
-63.6937 | [7 empty] | -80.3456
-50.8561 | [7 empty] | -64.1518
-29.4381 | [7 empty] | -37.1344
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
-72.9829 | [7 empty] | -92.0635
-145.5021 | [7 empty] | -183.5419
-211.6368 | [7 empty] | -266.9667
-265.7414 | [7 empty] | -335.2163
-302.9558 | [7 empty] | -382.16
-319.6642 | [7 empty] | -403.2365
-313.8442 | [7 empty] | -395.895
-285.274 | [7 empty] | -359.8554
-235.5759 | [7 empty] | -297.1644
-168.0939 | [7 empty] | -212.0401
-87.619 | [7 empty] | -110.5259
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
-87.2567 | [7 empty] | -110.0689
-168.8341 | [7 empty] | -212.9737
-239.4641 | [7 empty] | -302.069
-294.5762 | [7 empty] | -371.5896
-330.5312 | [7 empty] | -416.9446
-344.8143 | [7 empty] | -434.9619
-336.1767 | [7 empty] | -424.0661
-304.7221 | [7 empty] | -384.388
-251.9355 | [7 empty] | -317.801
-180.6509 | [7 empty] | -227.8799
-94.9502 | [7 empty] | -119.7738
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
-120.145 | [7 empty] | -151.5554
-234.2774 | [7 empty] | -295.5264
-333.7204 | [7 empty] | -420.9676
-410.7611 | [7 empty] | -518.1496
-459.3239 | [7 empty] | -579.4086
-475.5334 | [7 empty] | -599.8559
-458.0933 | [7 empty] | -577.8563
-408.44 | [7 empty] | -515.2217
-330.6458 | [7 empty] | -417.0891
-231.0753 | [7 empty] | -291.4872
-117.8241 | [7 empty] | -148.6278
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
-59.7069 | [7 empty] | -75.3166
-104.7309 | [7 empty] | -132.1115
-133.1252 | [7 empty] | -167.9292
-144.8639 | [7 empty] | -182.7368
-141.6436 | [7 empty] | -178.6746
-126.5178 | [7 empty] | -159.5943
-103.4062 | [7 empty] | -130.4405
-76.5467 | [7 empty] | -96.5589
-49.9581 | [7 empty] | -63.019
-26.9807 | [7 empty] | -34.0345
-9.9432 | [7 empty] | -12.5428
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
-0.13196 | [7 empty] | -0.16646
-7.3207 | [7 empty] | -9.2346
-16.4154 | [7 empty] | -20.7071
-25.1678 | [7 empty] | -31.7476
-31.657 | [7 empty] | -39.9333
-34.5586 | [7 empty] | -43.5935
-33.3013 | [7 empty] | -42.0076
-28.0964 | [7 empty] | -35.4419
-19.8437 | [7 empty] | -25.0316
-9.9348 | [7 empty] | -12.5321
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
-2.7382 | [7 empty] | -3.454
-8.5134 | [7 empty] | -10.7391
-11.8445 | [7 empty] | -14.941
-11.7265 | [7 empty] | -14.7922
-7.7112 | [7 empty] | -9.7272
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
-9.3743 | [7 empty] | -11.8251
-15.1299 | [7 empty] | -19.0854
-16.7989 | [7 empty] | -21.1908
-14.595 | [7 empty] | -18.4107
-9.362 | [7 empty] | -11.8096
-2.4509 | [7 empty] | -3.0917
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-9.5498 | [7 empty] | -12.0464
-19.377 | [7 empty] | -24.4429
-27.7134 | [7 empty] | -34.9587
-32.9609 | [7 empty] | -41.5781
-34.0233 | [7 empty] | -42.9183
-30.5676 | [7 empty] | -38.5591
-23.176 | [7 empty] | -29.2351
-13.3556 | [7 empty] | -16.8473
-3.3888 | [7 empty] | -4.2748
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-15.2267 | [7 empty] | -19.2076
-39.9431 | [7 empty] | -50.3857
-72.7719 | [7 empty] | -91.7972
-110.6903 | [7 empty] | -139.629
-149.2038 | [7 empty] | -188.2113
-182.7383 | [7 empty] | -230.513
-205.2343 | [7 empty] | -258.8903
-210.8811 | [7 empty] | -266.0134
-194.9101 | [7 empty] | -245.867
-154.3487 | [7 empty] | -194.7013
-88.636 | [7 empty] | -111.8088
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-198.3852 | [7 empty] | -250.2506
-392.9032 | [7 empty] | -495.623
-567.8095 | [7 empty] | -716.2564
-708.453 | [7 empty] | -893.6694
-802.6237 | [7 empty] | -1012.46
-841.6776 | [7 empty] | -1061.7241
-821.3385 | [7 empty] | -1036.0675
-742.1012 | [7 empty] | -936.1146
-609.2023 | [7 empty] | -768.4709
-432.1672 | [7 empty] | -545.1521
-223.987 | [7 empty] | -282.5457
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-207.211 | [7 empty] | -261.3838
-398.9818 | [7 empty] | -503.2907
-563.1961 | [7 empty] | -710.4369
-689.5613 | [7 empty] | -869.8387
-770.1392 | [7 empty] | -971.4828
-799.7384 | [7 empty] | -1008.8204
-776.1752 | [7 empty] | -979.0968
-700.4043 | [7 empty] | -883.5166
-576.5156 | [7 empty] | -727.2386
-411.5904 | [7 empty] | -519.1958
-215.4105 | [7 empty] | -271.727
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-257.67 | [7 empty] | -325.0347
-500.5537 | [7 empty] | -631.4174
-710.3933 | [7 empty] | -896.1171
-871.207 | [7 empty] | -1098.9735
-970.6989 | [7 empty] | -1224.4764
-1001.3741 | [7 empty] | -1263.1712
-961.2472 | [7 empty] | -1212.5537
-854.0656 | [7 empty] | -1077.3507
-689.0079 | [7 empty] | -869.1407
-479.8795 | [7 empty] | -605.3382
-243.8724 | [7 empty] | -307.6299
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-118.2236 | [7 empty] | -149.1317
-206.7374 | [7 empty] | -260.7864
-262.0081 | [7 empty] | -330.5069
-284.2791 | [7 empty] | -358.6004
-277.1583 | [7 empty] | -349.618
-246.8563 | [7 empty] | -311.3938
-201.1952 | [7 empty] | -253.7952
-148.524 | [7 empty] | -187.3537
-96.674 | [7 empty] | -121.9482
-52.0796 | [7 empty] | -65.6952
-19.1588 | [7 empty] | -24.1676
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.28091 | [7 empty] | -0.35436
-13.9624 | [7 empty] | -17.6128
-31.1902 | [7 empty] | -39.3446
-47.6801 | [7 empty] | -60.1454
-59.8112 | [7 empty] | -75.4481
-65.1231 | [7 empty] | -82.1488
-62.5952 | [7 empty] | -78.9599
-52.6829 | [7 empty] | -66.4562
-37.1236 | [7 empty] | -46.8291
-18.554 | [7 empty] | -23.4048
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-5.037 | [7 empty] | -6.3538
-15.5648 | [7 empty] | -19.634
-21.5942 | [7 empty] | -27.2397
-21.3306 | [7 empty] | -26.9072
-14.0046 | [7 empty] | -17.666
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-16.5153 | [7 empty] | -20.8331
-26.5843 | [7 empty] | -33.5345
-29.4544 | [7 empty] | -37.1549
-25.5425 | [7 empty] | -32.2203
-16.3616 | [7 empty] | -20.6392
-4.2603 | [7 empty] | -5.3741
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-16.3994 | [7 empty] | -20.6868
-33.2205 | [7 empty] | -41.9055
-47.4274 | [7 empty] | -59.8267
-56.3051 | [7 empty] | -71.0254
-58.0138 | [7 empty] | -73.1809
-52.0259 | [7 empty] | -65.6274
-39.3725 | [7 empty] | -49.666
-22.6455 | [7 empty] | -28.5658
-5.7306 | [7 empty] | -7.2287
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-25.5926 | [7 empty] | -32.2835
-67.0304 | [7 empty] | -84.5546
-121.9179 | [7 empty] | -153.7918
-185.1319 | [7 empty] | -233.5324
-249.1262 | [7 empty] | -314.2572
-304.607 | [7 empty] | -384.2428
-341.5344 | [7 empty] | -430.8245
-350.3486 | [7 empty] | -441.943
-323.28 | [7 empty] | -407.7976
-255.583 | [7 empty] | -322.4021
-146.5286 | [7 empty] | -184.8367
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-320.8904 | [7 empty] | -404.7833
-634.5863 | [7 empty] | -800.4912
-915.7276 | [7 empty] | -1155.1335
-1140.8703 | [7 empty] | -1439.1371
-1290.6316 | [7 empty] | -1628.0517
-1351.4647 | [7 empty] | -1704.7888
-1316.9014 | [7 empty] | -1661.1894
-1188.1462 | [7 empty] | -1498.7727
-973.9739 | [7 empty] | -1228.6075
-689.9532 | [7 empty] | -870.3331
-357.0867 | [7 empty] | -450.4427
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-324.1403 | [7 empty] | -408.8828
-623.3234 | [7 empty] | -786.2837
-878.7405 | [7 empty] | -1108.4766
-1074.5261 | [7 empty] | -1355.448
-1198.5585 | [7 empty] | -1511.9071
-1243.0445 | [7 empty] | -1568.0234
-1204.8973 | [7 empty] | -1519.9032
-1085.9091 | [7 empty] | -1369.8069
-892.7148 | [7 empty] | -1126.1043
-636.541 | [7 empty] | -802.9569
-332.7269 | [7 empty] | -419.7143
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-391.4383 | [7 empty] | -493.7751
-759.5509 | [7 empty] | -958.1263
-1076.7438 | [7 empty] | -1358.2455
-1318.9983 | [7 empty] | -1663.8345
-1467.9765 | [7 empty] | -1851.7612
-1512.6724 | [7 empty] | -1908.1423
-1450.4408 | [7 empty] | -1829.641
-1287.2852 | [7 empty] | -1623.8303
-1037.3579 | [7 empty] | -1308.5626
-721.7044 | [7 empty] | -910.3852
-366.3641 | [7 empty] | -462.1456
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-175.0059 | [7 empty] | -220.759
-305.7259 | [7 empty] | -385.6542
-387.0713 | [7 empty] | -488.2664
-419.5516 | [7 empty] | -529.2383
-408.6337 | [7 empty] | -515.4661
-363.5948 | [7 empty] | -458.6523
-296.0464 | [7 empty] | -373.4441
-218.3274 | [7 empty] | -275.4065
-141.968 | [7 empty] | -179.0838
-76.4033 | [7 empty] | -96.378
-28.0766 | [7 empty] | -35.4169
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.40594 | [7 empty] | -0.51207
-20.3819 | [7 empty] | -25.7105
-45.4929 | [7 empty] | -57.3864
-69.481 | [7 empty] | -87.646
-87.0781 | [7 empty] | -109.8436
-94.7233 | [7 empty] | -119.4876
-90.9613 | [7 empty] | -114.7421
-76.4854 | [7 empty] | -96.4816
-53.8452 | [7 empty] | -67.9224
-26.8844 | [7 empty] | -33.913
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-7.2428 | [7 empty] | -9.1364
-22.3707 | [7 empty] | -28.2192
-31.0108 | [7 empty] | -39.1183
-30.6055 | [7 empty] | -38.6069
-20.0751 | [7 empty] | -25.3235
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-23.397 | [7 empty] | -29.5139
-37.6334 | [7 empty] | -47.4722
-41.6629 | [7 empty] | -52.5551
-36.0997 | [7 empty] | -45.5376
-23.1041 | [7 empty] | -29.1444
-6.008 | [7 empty] | -7.5788
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-23.0113 | [7 empty] | -29.0273
-46.5823 | [7 empty] | -58.7606
-66.4538 | [7 empty] | -83.8273
-78.8329 | [7 empty] | -99.4428
-81.1631 | [7 empty] | -102.3823
-72.7298 | [7 empty] | -91.7441
-54.9981 | [7 empty] | -69.3767
-31.607 | [7 empty] | -39.8703
-7.9893 | [7 empty] | -10.0781
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-35.5875 | [7 empty] | -44.8915
-93.1456 | [7 empty] | -117.4974
-169.2959 | [7 empty] | -213.5563
-256.8887 | [7 empty] | -324.0491
-345.4357 | [7 empty] | -435.7457
-422.0582 | [7 empty] | -532.4002
-472.8816 | [7 empty] | -596.5108
-484.7353 | [7 empty] | -611.4634
-446.9616 | [7 empty] | -563.8143
-353.1109 | [7 empty] | -445.4275
-202.2963 | [7 empty] | -255.1842
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-438.7421 | [7 empty] | -553.4459
-867.0664 | [7 empty] | -1093.7504
-1250.3654 | [7 empty] | -1577.2583
-1556.7423 | [7 empty] | -1963.7337
-1759.9223 | [7 empty] | -2220.0327
-1841.6523 | [7 empty] | -2323.13
-1793.3661 | [7 empty] | -2262.2199
-1616.9602 | [7 empty] | -2039.6949
-1324.6205 | [7 empty] | -1670.9265
-937.7331 | [7 empty] | -1182.8921
-485.0079 | [7 empty] | -611.8074
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-436.3689 | [7 empty] | -550.4522
-838.6253 | [7 empty] | -1057.8738
-1181.5411 | [7 empty] | -1490.4408
-1443.9077 | [7 empty] | -1821.3999
-1609.5957 | [7 empty] | -2030.405
-1668.3233 | [7 empty] | -2104.4863
-1616.1455 | [7 empty] | -2038.6672
-1455.6655 | [7 empty] | -1836.2317
-1195.9676 | [7 empty] | -1508.6388
-852.2602 | [7 empty] | -1075.0733
-445.2181 | [7 empty] | -561.6149
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-519.5299 | [7 empty] | -655.3547
-1007.5328 | [7 empty] | -1270.94
-1427.479 | [7 empty] | -1800.6761
-1747.6609 | [7 empty] | -2204.5658
-1943.9648 | [7 empty] | -2452.1909
-2002.0333 | [7 empty] | -2525.4407
-1918.5993 | [7 empty] | -2420.1939
-1701.8359 | [7 empty] | -2146.7604
-1370.6636 | [7 empty] | -1729.0071
-953.0628 | [7 empty] | -1202.2295
-483.5428 | [7 empty] | -609.9592
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-229.2503 | [7 empty] | -289.185
-400.2807 | [7 empty] | -504.9292
-506.5211 | [7 empty] | -638.945
-548.7397 | [7 empty] | -692.2011
-534.183 | [7 empty] | -673.8387
-475.0605 | [7 empty] | -599.2593
-386.6043 | [7 empty] | -487.6773
-284.9647 | [7 empty] | -359.4653
-185.2032 | [7 empty] | -233.6223
-99.6191 | [7 empty] | -125.6634
-36.5875 | [7 empty] | -46.1528
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.52522 | [7 empty] | -0.66253
-26.5059 | [7 empty] | -33.4355
-59.1359 | [7 empty] | -74.5962
-90.2744 | [7 empty] | -113.8756
-113.0823 | [7 empty] | -142.6463
-122.95 | [7 empty] | -155.0937
-118.0085 | [7 empty] | -148.8604
-99.1788 | [7 empty] | -125.108
-69.7861 | [7 empty] | -88.0308
-34.825 | [7 empty] | -43.9296
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-9.3438 | [7 empty] | -11.7867
-28.8522 | [7 empty] | -36.3953
-39.9779 | [7 empty] | -50.4297
-39.4367 | [7 empty] | -49.7469
-25.8545 | [7 empty] | -32.6139
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-29.9395 | [7 empty] | -37.7668
-48.1368 | [7 empty] | -60.7216
-53.2673 | [7 empty] | -67.1934
-46.1336 | [7 empty] | -58.1947
-29.5117 | [7 empty] | -37.2271
-7.6688 | [7 empty] | -9.6737
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-29.2896 | [7 empty] | -36.9471
-59.2687 | [7 empty] | -74.7637
-84.5166 | [7 empty] | -106.6124
-100.2176 | [7 empty] | -126.4182
-103.1355 | [7 empty] | -130.099
-92.3791 | [7 empty] | -116.5305
-69.8262 | [7 empty] | -88.0815
-40.1103 | [7 empty] | -50.5967
-10.1324 | [7 empty] | -12.7814
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-45.0665 | [7 empty] | -56.8486
-117.9102 | [7 empty] | -148.7364
-214.2189 | [7 empty] | -270.2239
-324.9201 | [7 empty] | -409.8665
-436.7357 | [7 empty] | -550.915
-533.3887 | [7 empty] | -672.8367
-597.3709 | [7 empty] | -753.5463
-612.0922 | [7 empty] | -772.1163
-564.1613 | [7 empty] | -711.6544
-445.5179 | [7 empty] | -561.9932
-255.1303 | [7 empty] | -321.831
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-550.231 | [7 empty] | -694.0823
-1086.9719 | [7 empty] | -1371.1476
-1566.8699 | [7 empty] | -1976.5091
-1950.0377 | [7 empty] | -2459.8514
-2203.6897 | [7 empty] | -2779.8177
-2305.1313 | [7 empty] | -2907.78
-2243.8225 | [7 empty] | -2830.4427
-2022.3243 | [7 empty] | -2551.0365
-1656.0568 | [7 empty] | -2089.0128
-1171.9137 | [7 empty] | -1478.2964
-605.8955 | [7 empty] | -764.2995
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-542.2692 | [7 empty] | -684.0389
-1041.7652 | [7 empty] | -1314.1221
-1467.2065 | [7 empty] | -1850.7899
-1792.3491 | [7 empty] | -2260.9371
-1997.2898 | [7 empty] | -2519.4571
-2069.4074 | [7 empty] | -2610.4289
-2003.9555 | [7 empty] | -2527.8655
-1804.3112 | [7 empty] | -2276.0266
-1481.8759 | [7 empty] | -1869.2944
-1055.6196 | [7 empty] | -1331.5986
-551.2526 | [7 empty] | -695.3709
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-640.0871 | [7 empty] | -807.4301
-1240.903 | [7 empty] | -1565.3221
-1757.5122 | [7 empty] | -2216.9925
-2150.9782 | [7 empty] | -2713.3254
-2391.7608 | [7 empty] | -3017.0577
-2462.3597 | [7 empty] | -3106.1138
-2358.9334 | [7 empty] | -2975.648
-2091.7059 | [7 empty] | -2638.5571
-1684.0914 | [7 empty] | -2124.3768
-1170.5995 | [7 empty] | -1476.6386
-593.7089 | [7 empty] | -748.9269
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-280.1701 | [7 empty] | -353.4172
-489.0305 | [7 empty] | -616.8817
-618.6253 | [7 empty] | -780.3574
-669.9698 | [7 empty] | -845.1253
-651.9854 | [7 empty] | -822.4391
-579.6367 | [7 empty] | -731.1757
-471.5557 | [7 empty] | -594.8382
-347.4695 | [7 empty] | -438.3111
-225.7527 | [7 empty] | -284.773
-121.3904 | [7 empty] | -153.1264
-44.5678 | [7 empty] | -56.2195
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.63703 | [7 empty] | -0.80357
-32.2456 | [7 empty] | -40.6758
-71.9214 | [7 empty] | -90.7244
-109.7588 | [7 empty] | -138.4539
-137.4466 | [7 empty] | -173.3804
-149.3936 | [7 empty] | -188.4508
-143.3444 | [7 empty] | -180.82
-120.4341 | [7 empty] | -151.9201
-84.715 | [7 empty] | -106.8627
-42.2607 | [7 empty] | -53.3093
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-11.3095 | [7 empty] | -14.2662
-34.9155 | [7 empty] | -44.0438
-48.3654 | [7 empty] | -61.0099
-47.6961 | [7 empty] | -60.1656
-31.2592 | [7 empty] | -39.4315
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-36.0479 | [7 empty] | -45.4722
-57.9423 | [7 empty] | -73.0906
-64.0993 | [7 empty] | -80.8573
-55.4985 | [7 empty] | -70.0079
-35.4914 | [7 empty] | -44.7701
-9.2185 | [7 empty] | -11.6286
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-35.1433 | [7 empty] | -44.3312
-71.0956 | [7 empty] | -89.6827
-101.3538 | [7 empty] | -127.8515
-120.149 | [7 empty] | -151.5605
-123.6123 | [7 empty] | -155.9292
-110.6888 | [7 empty] | -139.627
-83.6419 | [7 empty] | -105.509
-48.0321 | [7 empty] | -60.5895
-12.1287 | [7 empty] | -15.2996
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-53.892 | [7 empty] | -67.9814
-140.965 | [7 empty] | -177.8185
-256.0353 | [7 empty] | -322.9727
-388.2394 | [7 empty] | -489.7399
-521.7021 | [7 empty] | -658.0948
-636.9838 | [7 empty] | -803.5155
-713.197 | [7 empty] | -899.6537
-730.5723 | [7 empty] | -921.5716
-673.1793 | [7 empty] | -849.1739
-531.4639 | [7 empty] | -670.4087
-304.2644 | [7 empty] | -383.8106
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-653.7404 | [7 empty] | -824.6529
-1291.1138 | [7 empty] | -1628.6599
-1860.6509 | [7 empty] | -2347.0956
-2315.0527 | [7 empty] | -2920.2952
-2615.4981 | [7 empty] | -3299.2884
-2735.1802 | [7 empty] | -3450.26
-2661.7378 | [7 empty] | -3357.617
-2398.3597 | [7 empty] | -3025.3818
-1963.4763 | [7 empty] | -2476.8034
-1389.0987 | [7 empty] | -1752.2618
-717.9961 | [7 empty] | -905.7075
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-640.3053 | [7 empty] | -807.7054
-1229.797 | [7 empty] | -1551.3125
-1731.5937 | [7 empty] | -2184.298
-2114.797 | [7 empty] | -2667.6851
-2356.0183 | [7 empty] | -2971.9708
-2440.4799 | [7 empty] | -3078.5138
-2362.7033 | [7 empty] | -2980.4035
-2126.79 | [7 empty] | -2682.8135
-1746.2934 | [7 empty] | -2202.8407
-1243.67 | [7 empty] | -1568.8125
-649.2926 | [7 empty] | -819.0423
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-751.3616 | [7 empty] | -947.796
-1456.2771 | [7 empty] | -1837.0031
-2062.0571 | [7 empty] | -2601.157
-2523.1009 | [7 empty] | -3182.7351
-2804.8702 | [7 empty] | -3538.1697
-2886.9757 | [7 empty] | -3641.7406
-2765.0571 | [7 empty] | -3487.9479
-2451.2409 | [7 empty] | -3092.0882
-1973.0957 | [7 empty] | -2488.9377
-1371.1597 | [7 empty] | -1729.6328
-695.2649 | [7 empty] | -877.0335
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-327.0268 | [7 empty] | -412.5241
-570.6884 | [7 empty] | -719.8879
-721.7579 | [7 empty] | -910.4528
-781.4838 | [7 empty] | -985.7933
-760.3325 | [7 empty] | -959.1122
-675.8068 | [7 empty] | -852.4883
-549.6684 | [7 empty] | -693.3725
-404.9351 | [7 empty] | -510.8005
-263.0283 | [7 empty] | -331.7938
-141.4013 | [7 empty] | -178.3689
-51.9019 | [7 empty] | -65.4711
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.73975 | [7 empty] | -0.93314
-37.5178 | [7 empty] | -47.3264
-83.664 | [7 empty] | -105.5369
-127.6515 | [7 empty] | -161.0245
-159.8178 | [7 empty] | -201.6002
-173.6709 | [7 empty] | -219.075
-166.6015 | [7 empty] | -210.1575
-139.9429 | [7 empty] | -176.5292
-98.4155 | [7 empty] | -124.1451
-49.0837 | [7 empty] | -61.916
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-13.1112 | [7 empty] | -16.539
-40.4726 | [7 empty] | -51.0537
-56.0516 | [7 empty] | -70.7056
-55.2639 | [7 empty] | -69.7119
-36.2106 | [7 empty] | -45.6775
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-41.6337 | [7 empty] | -52.5183
-66.9075 | [7 empty] | -84.3997
-74.0019 | [7 empty] | -93.3488
-64.0587 | [7 empty] | -80.8061
-40.9565 | [7 empty] | -51.6641
-10.6347 | [7 empty] | -13.415
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-40.4875 | [7 empty] | -51.0725
-81.8917 | [7 empty] | -103.3013
-116.7212 | [7 empty] | -147.2366
-138.3381 | [7 empty] | -174.5049
-142.2965 | [7 empty] | -179.4982
-127.3933 | [7 empty] | -160.6988
-96.2446 | [7 empty] | -121.4066
-55.2574 | [7 empty] | -69.7038
-13.9492 | [7 empty] | -17.596
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-61.9361 | [7 empty] | -78.1285
-161.9755 | [7 empty] | -204.322
-294.1387 | [7 empty] | -371.0377
-445.9285 | [7 empty] | -562.5111
-599.1026 | [7 empty] | -755.7307
-731.3411 | [7 empty] | -922.5415
-818.68 | [7 empty] | -1032.714
-838.4575 | [7 empty] | -1057.662
-772.4347 | [7 empty] | -974.3784
-609.7025 | [7 empty] | -769.1018
-348.9861 | [7 empty] | -440.2242
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-747.7689 | [7 empty] | -943.2641
-1476.5313 | [7 empty] | -1862.5526
-2127.4479 | [7 empty] | -2683.6435
-2646.4936 | [7 empty] | -3338.3874
-2989.3752 | [7 empty] | -3770.9112
-3125.5621 | [7 empty] | -3942.7026
-3041.0514 | [7 empty] | -3836.0975
-2739.6128 | [7 empty] | -3455.8515
-2242.4204 | [7 empty] | -2828.6741
-1586.1384 | [7 empty] | -2000.8151
-819.6841 | [7 empty] | -1033.9806
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-729.0555 | [7 empty] | -919.6583
-1399.9937 | [7 empty] | -1766.0051
-1970.8686 | [7 empty] | -2486.1284
-2406.5751 | [7 empty] | -3035.7451
-2680.5786 | [7 empty] | -3381.3834
-2776.1593 | [7 empty] | -3501.9526
-2687.1859 | [7 empty] | -3389.7182
-2418.425 | [7 empty] | -3050.693
-1985.3853 | [7 empty] | -2504.4402
-1413.6841 | [7 empty] | -1783.2747
-737.9164 | [7 empty] | -930.8358
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-851.7395 | [7 empty] | -1074.4165
-1650.5316 | [7 empty] | -2082.0432
-2336.697 | [7 empty] | -2947.5982
-2858.6323 | [7 empty] | -3605.9871
-3177.3021 | [7 empty] | -4007.9693
-3269.7234 | [7 empty] | -4124.553
-3131.0806 | [7 empty] | -3949.6637
-2775.2269 | [7 empty] | -3500.7764
-2233.4852 | [7 empty] | -2817.4029
-1551.8347 | [7 empty] | -1957.5432
-786.738 | [7 empty] | -992.4211
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-369.141 | [7 empty] | -465.6485
-644.0699 | [7 empty] | -812.4542
-814.4233 | [7 empty] | -1027.3445
-881.6644 | [7 empty] | -1112.1649
-857.653 | [7 empty] | -1081.876
-762.1761 | [7 empty] | -961.4379
-619.8096 | [7 empty] | -781.8514
-456.5284 | [7 empty] | -575.8822
-296.4895 | [7 empty] | -374.0031
-159.3617 | [7 empty] | -201.0248
-58.4835 | [7 empty] | -73.7733
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.83188 | [7 empty] | -1.0494
-42.2461 | [7 empty] | -53.2908
-94.1934 | [7 empty] | -118.8192
-143.6931 | [7 empty] | -181.2599
-179.8713 | [7 empty] | -226.8965
-195.4296 | [7 empty] | -246.5223
-187.4427 | [7 empty] | -236.4473
-157.4223 | [7 empty] | -198.5784
-110.6889 | [7 empty] | -139.6272
-55.195 | [7 empty] | -69.625
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-14.723 | [7 empty] | -18.5721
-45.4429 | [7 empty] | -57.3233
-62.925 | [7 empty] | -79.376
-62.0304 | [7 empty] | -78.2475
-40.6371 | [7 empty] | -51.2612
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-46.6159 | [7 empty] | -58.803
-74.9026 | [7 empty] | -94.485
-82.8314 | [7 empty] | -104.4866
-71.6901 | [7 empty] | -90.4326
-45.8278 | [7 empty] | -57.8089
-11.8967 | [7 empty] | -15.007
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-45.2447 | [7 empty] | -57.0734
-91.5003 | [7 empty] | -115.4219
-130.3961 | [7 empty] | -164.4865
-154.521 | [7 empty] | -194.9187
-158.9172 | [7 empty] | -200.4642
-142.2505 | [7 empty] | -179.4402
-107.4517 | [7 empty] | -135.5436
-61.6815 | [7 empty] | -77.8074
-15.5675 | [7 empty] | -19.6375
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-69.082 | [7 empty] | -87.1427
-180.6371 | [7 empty] | -227.8625
-327.9765 | [7 empty] | -413.722
-497.1506 | [7 empty] | -627.1246
-667.8147 | [7 empty] | -842.4068
-815.0923 | [7 empty] | -1028.1884
-912.2903 | [7 empty] | -1150.7975
-934.183 | [7 empty] | -1178.4138
-860.4879 | [7 empty] | -1085.4521
-679.0989 | [7 empty] | -856.6411
-388.6467 | [7 empty] | -490.2536
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-830.9531 | [7 empty] | -1048.1957
-1640.5355 | [7 empty] | -2069.4337
-2363.3916 | [7 empty] | -2981.2718
-2939.5538 | [7 empty] | -3708.0646
-3319.8989 | [7 empty] | -4187.8463
-3470.6156 | [7 empty] | -4377.966
-3376.262 | [7 empty] | -4258.9449
-3041.1348 | [7 empty] | -3836.2027
-2488.8439 | [7 empty] | -3139.5221
-1760.1751 | [7 empty] | -2220.3517
-909.4847 | [7 empty] | -1147.2585
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-807.2327 | [7 empty] | -1018.2739
-1549.8871 | [7 empty] | -1955.0863
-2181.561 | [7 empty] | -2751.9038
-2663.4519 | [7 empty] | -3359.7791
-2966.2638 | [7 empty] | -3741.7576
-3071.5775 | [7 empty] | -3874.6043
-2972.6976 | [7 empty] | -3749.8735
-2674.9868 | [7 empty] | -3374.3297
-2195.6842 | [7 empty] | -2769.7192
-1563.1964 | [7 empty] | -1971.8751
-815.8387 | [7 empty] | -1029.1299
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-939.7652 | [7 empty] | -1185.4555
-1820.8494 | [7 empty] | -2296.8884
-2577.4491 | [7 empty] | -3251.292
-3152.7064 | [7 empty] | -3976.9434
-3503.6551 | [7 empty] | -4419.6433
-3605.0519 | [7 empty] | -4547.5491
-3451.6955 | [7 empty] | -4354.0995
-3058.965 | [7 empty] | -3858.6945
-2461.4836 | [7 empty] | -3105.0087
-1710.0043 | [7 empty] | -2157.0643
-866.8014 | [7 empty] | -1093.4162
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-405.9019 | [7 empty] | -512.02
-708.1109 | [7 empty] | -893.2379
-895.2777 | [7 empty] | -1129.3372
-969.0588 | [7 empty] | -1222.4075
-942.5354 | [7 empty] | -1188.9499
-837.4921 | [7 empty] | -1056.4443
-680.9622 | [7 empty] | -858.9916
-501.5009 | [7 empty] | -632.6123
-325.6509 | [7 empty] | -410.7884
-175.011 | [7 empty] | -220.7655
-64.2171 | [7 empty] | -81.0059
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.91209 | [7 empty] | -1.1505
-46.3618 | [7 empty] | -58.4825
-103.3569 | [7 empty] | -130.3784
-157.6509 | [7 empty] | -198.8669
-197.3164 | [7 empty] | -248.9024
-214.3542 | [7 empty] | -270.3945
-205.5656 | [7 empty] | -259.3083
-172.6188 | [7 empty] | -217.7479
-121.3572 | [7 empty] | -153.0845
-60.5059 | [7 empty] | -76.3244
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-16.1213 | [7 empty] | -20.3361
-49.7542 | [7 empty] | -62.7619
-68.886 | [7 empty] | -86.8954
-67.8974 | [7 empty] | -85.6484
-44.4744 | [7 empty] | -56.1016
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-50.9221 | [7 empty] | -64.2351
-81.8116 | [7 empty] | -103.2002
-90.4597 | [7 empty] | -114.1094
-78.2819 | [7 empty] | -98.7477
-50.0346 | [7 empty] | -63.1156
-12.9864 | [7 empty] | -16.3815
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-49.3458 | [7 empty] | -62.2467
-99.782 | [7 empty] | -125.8688
-142.18 | [7 empty] | -179.3512
-168.4632 | [7 empty] | -212.5059
-173.2334 | [7 empty] | -218.5232
-155.0449 | [7 empty] | -195.5795
-117.1006 | [7 empty] | -147.7152
-67.2112 | [7 empty] | -84.7828
-16.9603 | [7 empty] | -21.3943
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-75.2263 | [7 empty] | -94.8933
-196.6791 | [7 empty] | -248.0985
-357.0579 | [7 empty] | -450.4064
-541.1629 | [7 empty] | -682.6434
-726.8419 | [7 empty] | -916.866
-887.0228 | [7 empty] | -1118.9241
-992.6701 | [7 empty] | -1252.1917
-1016.3606 | [7 empty] | -1282.0758
-936.062 | [7 empty] | -1180.7841
-738.6469 | [7 empty] | -931.7571
-422.671 | [7 empty] | -533.1733
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-902.0865 | [7 empty] | -1137.926
-1780.7479 | [7 empty] | -2246.303
-2565.0602 | [7 empty] | -3235.6642
-3189.9831 | [7 empty] | -4023.9656
-3602.2758 | [7 empty] | -4544.0472
-3765.3364 | [7 empty] | -4749.738
-3662.5084 | [7 empty] | -4620.0269
-3298.5526 | [7 empty] | -4160.9193
-2699.173 | [7 empty] | -3404.8391
-1908.685 | [7 empty] | -2407.6876
-986.0956 | [7 empty] | -1243.8984
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-873.7031 | [7 empty] | -1102.1222
-1677.3033 | [7 empty] | -2115.8139
-2360.6153 | [7 empty] | -2977.7697
-2881.7019 | [7 empty] | -3635.088
-3208.9308 | [7 empty] | -4047.8669
-3322.4501 | [7 empty] | -4191.0645
-3215.0978 | [7 empty] | -4055.6462
-2892.7546 | [7 empty] | -3649.0303
-2374.1402 | [7 empty] | -2994.8304
-1690.0384 | [7 empty] | -2131.8785
-881.9294 | [7 empty] | -1112.4992
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-1014.1621 | [7 empty] | -1279.3025
-1964.7603 | [7 empty] | -2478.4231
-2780.8217 | [7 empty] | -3507.8339
-3401.0583 | [7 empty] | -4290.2239
-3779.1962 | [7 empty] | -4767.2214
-3888.098 | [7 empty] | -4904.5942
-3722.2522 | [7 empty] | -4695.39
-3298.3405 | [7 empty] | -4160.6518
-2653.7844 | [7 empty] | -3347.5842
-1843.3746 | [7 empty] | -2325.3027
-934.2942 | [7 empty] | -1178.5542
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-436.7763 | [7 empty] | -550.9662
-761.8826 | [7 empty] | -961.0676
-963.1484 | [7 empty] | -1214.9519
-1042.3995 | [7 empty] | -1314.9223
-1013.7489 | [7 empty] | -1278.7813
-900.6625 | [7 empty] | -1136.1298
-732.2393 | [7 empty] | -923.6744
-539.2006 | [7 empty] | -680.1681
-350.0898 | [7 empty] | -441.6165
-188.1224 | [7 empty] | -237.3048
-69.0195 | [7 empty] | -87.0638
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.97922 | [7 empty] | -1.2352
-49.8053 | [7 empty] | -62.8263
-111.0217 | [7 empty] | -140.0469
-169.3226 | [7 empty] | -213.5899
-211.9001 | [7 empty] | -267.2988
-230.1703 | [7 empty] | -290.3455
-220.7074 | [7 empty] | -278.4087
-185.312 | [7 empty] | -233.7596
-130.2656 | [7 empty] | -164.322
-64.9395 | [7 empty] | -81.9171
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-17.2861 | [7 empty] | -21.8053
-53.3442 | [7 empty] | -67.2904
-73.8481 | [7 empty] | -93.1548
-72.7799 | [7 empty] | -91.8074
-47.6668 | [7 empty] | -60.1287
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-54.49 | [7 empty] | -68.7357
-87.5342 | [7 empty] | -110.419
-96.7764 | [7 empty] | -122.0774
-83.7385 | [7 empty] | -105.6309
-53.516 | [7 empty] | -67.5071
-13.8879 | [7 empty] | -17.5187
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-52.7315 | [7 empty] | -66.5175
-106.6168 | [7 empty] | -134.4904
-151.9021 | [7 empty] | -191.615
-179.9624 | [7 empty] | -227.0113
-185.0374 | [7 empty] | -233.4132
-165.5908 | [7 empty] | -208.8825
-125.0514 | [7 empty] | -157.7446
-71.7663 | [7 empty] | -90.5288
-18.1072 | [7 empty] | -22.8411
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-80.2797 | [7 empty] | -101.2679
-209.869 | [7 empty] | -264.7367
-380.9612 | [7 empty] | -480.5589
-577.3271 | [7 empty] | -728.2622
-775.3283 | [7 empty] | -978.0285
-946.0892 | [7 empty] | -1193.4328
-1058.6538 | [7 empty] | -1335.426
-1083.7985 | [7 empty] | -1367.1445
-998.061 | [7 empty] | -1258.992
-787.4827 | [7 empty] | -993.3605
-450.5658 | [7 empty] | -568.3607
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-960.1374 | [7 empty] | -1211.1537
-1895.1351 | [7 empty] | -2390.5952
-2729.5291 | [7 empty] | -3443.1314
-3394.1496 | [7 empty] | -4281.509
-3832.4105 | [7 empty] | -4834.3479
-4005.4503 | [7 empty] | -5052.6268
-3895.6392 | [7 empty] | -4914.107
-3508.1332 | [7 empty] | -4425.2921
-2870.3572 | [7 empty] | -3620.7774
-2029.5142 | [7 empty] | -2560.1061
-1048.4058 | [7 empty] | -1322.4988
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-927.5027 | [7 empty] | -1169.9871
-1780.3944 | [7 empty] | -2245.857
-2505.4349 | [7 empty] | -3160.4505
-3058.16 | [7 empty] | -3857.679
-3405.0602 | [7 empty] | -4295.272
-3525.1388 | [7 empty] | -4446.7438
-3410.871 | [7 empty] | -4302.6019
-3068.5702 | [7 empty] | -3870.8108
-2518.1652 | [7 empty] | -3176.5091
-1792.3707 | [7 empty] | -2260.9644
-935.23 | [7 empty] | -1179.7346
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-1073.8511 | [7 empty] | -1354.5965
-2080.1773 | [7 empty] | -2624.0145
-2943.8654 | [7 empty] | -3713.5034
-3600.0864 | [7 empty] | -4541.2855
-3999.9296 | [7 empty] | -5045.6628
-4114.7569 | [7 empty] | -5190.5104
-3938.8268 | [7 empty] | -4968.5854
-3489.8818 | [7 empty] | -4402.2693
-2807.5986 | [7 empty] | -3541.6113
-1950.0115 | [7 empty] | -2459.8184
-988.2375 | [7 empty] | -1246.6002
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-461.3164 | [7 empty] | -581.922
-804.6052 | [7 empty] | -1014.9596
-1017.0511 | [7 empty] | -1282.9469
-1100.6229 | [7 empty] | -1388.3674
-1070.2605 | [7 empty] | -1350.0672
-950.7711 | [7 empty] | -1199.3387
-772.8971 | [7 empty] | -974.9617
-569.0806 | [7 empty] | -717.8598
-369.4516 | [7 empty] | -466.0402
-198.5057 | [7 empty] | -250.4026
-72.8211 | [7 empty] | -91.8593
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-1.0323 | [7 empty] | -1.3022
-52.5267 | [7 empty] | -66.2591
-117.0765 | [7 empty] | -147.6847
-178.5387 | [7 empty] | -225.2155
-223.4108 | [7 empty] | -281.8189
-242.6485 | [7 empty] | -306.086
-232.6486 | [7 empty] | -293.4718
-195.3179 | [7 empty] | -246.3815
-137.285 | [7 empty] | -173.1765
-68.4314 | [7 empty] | -86.322
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-18.2002 | [7 empty] | -22.9585
-56.1606 | [7 empty] | -70.8431
-77.7394 | [7 empty] | -98.0634
-76.6071 | [7 empty] | -96.6351
-50.168 | [7 empty] | -63.2839
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-57.2678 | [7 empty] | -72.2397
-91.9875 | [7 empty] | -116.0366
-101.6896 | [7 empty] | -128.2752
-87.9809 | [7 empty] | -110.9824
-56.2213 | [7 empty] | -70.9197
-14.5881 | [7 empty] | -18.402
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-55.3525 | [7 empty] | -69.8238
-111.9055 | [7 empty] | -141.1618
-159.4213 | [7 empty] | -201.1001
-188.8518 | [7 empty] | -238.2248
-194.158 | [7 empty] | -244.9182
-173.7354 | [7 empty] | -219.1564
-131.1888 | [7 empty] | -165.4865
-75.2808 | [7 empty] | -94.962
-18.9917 | [7 empty] | -23.9568
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-84.1691 | [7 empty] | -106.1741
-220.0153 | [7 empty] | -277.5357
-399.3397 | [7 empty] | -503.7423
-605.1187 | [7 empty] | -763.3196
-812.5705 | [7 empty] | -1025.0072
-991.4351 | [7 empty] | -1250.6338
-1109.2845 | [7 empty] | -1399.2935
-1135.5188 | [7 empty] | -1432.3864
-1045.5857 | [7 empty] | -1318.9414
-824.8981 | [7 empty] | -1040.5578
-471.9263 | [7 empty] | -595.3057
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-1004.264 | [7 empty] | -1266.8167
-1982.0381 | [7 empty] | -2500.218
-2854.4129 | [7 empty] | -3600.6646
-3549.0924 | [7 empty] | -4476.9597
-4006.9657 | [7 empty] | -5054.5385
-4187.4751 | [7 empty] | -5282.2398
-4072.2734 | [7 empty] | -5136.9201
-3666.837 | [7 empty] | -4625.4871
-2999.9141 | [7 empty] | -3784.2054
-2120.9104 | [7 empty] | -2675.3968
-1095.5115 | [7 empty] | -1381.9198
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-967.8513 | [7 empty] | -1220.8844
-1857.6655 | [7 empty] | -2343.3296
-2613.9193 | [7 empty] | -3297.2969
-3190.2672 | [7 empty] | -4024.3239
-3551.8076 | [7 empty] | -4480.3848
-3676.7042 | [7 empty] | -4637.9341
-3557.1779 | [7 empty] | -4487.1591
-3199.8839 | [7 empty] | -4036.4548
-2625.6706 | [7 empty] | -3312.1204
-1868.7092 | [7 empty] | -2357.2607
-974.9676 | [7 empty] | -1229.861
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-1117.9667 | [7 empty] | -1410.2456
-2165.4266 | [7 empty] | -2731.5511
-3064.2156 | [7 empty] | -3865.3178
-3746.9042 | [7 empty] | -4726.4869
-4162.6538 | [7 empty] | -5250.9293
-4281.7415 | [7 empty] | -5401.1511
-4098.2785 | [7 empty] | -5169.7239
-3630.8111 | [7 empty] | -4580.0427
-2920.6956 | [7 empty] | -3684.2762
-2028.3683 | [7 empty] | -2558.6606
-1027.849 | [7 empty] | -1296.5676
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-479.1665 | [7 empty] | -604.4388
-835.6592 | [7 empty] | -1054.1322
-1056.2042 | [7 empty] | -1332.336
-1142.8846 | [7 empty] | -1441.6779
-1111.2508 | [7 empty] | -1401.7739
-987.0913 | [7 empty] | -1245.1543
-802.3461 | [7 empty] | -1012.1098
-590.7076 | [7 empty] | -745.141
-383.4555 | [7 empty] | -483.7053
-206.0103 | [7 empty] | -259.8692
-75.5667 | [7 empty] | -95.3227
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-1.0705 | [7 empty] | -1.3504
-54.4864 | [7 empty] | -68.7312
-121.4335 | [7 empty] | -153.1808
-185.1658 | [7 empty] | -233.5751
-231.6816 | [7 empty] | -292.252
-251.6078 | [7 empty] | -317.3876
-241.2159 | [7 empty] | -304.2789
-202.4914 | [7 empty] | -255.4303
-142.3135 | [7 empty] | -179.5196
-70.9311 | [7 empty] | -89.4752
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-18.8506 | [7 empty] | -23.7789
-58.1628 | [7 empty] | -73.3687
-80.5034 | [7 empty] | -101.55
-79.3234 | [7 empty] | -100.0615
-51.9419 | [7 empty] | -65.5215
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-59.2152 | [7 empty] | -74.6963
-95.1069 | [7 empty] | -119.9715
-105.1283 | [7 empty] | -132.6128
-90.9475 | [7 empty] | -114.7246
-58.1115 | [7 empty] | -73.304
-15.0769 | [7 empty] | -19.0186
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-57.171 | [7 empty] | -72.1176
-115.5714 | [7 empty] | -145.7862
-164.6287 | [7 empty] | -207.6689
-195.0025 | [7 empty] | -245.9835
-200.4629 | [7 empty] | -252.8716
-179.3605 | [7 empty] | -226.2522
-135.4238 | [7 empty] | -170.8287
-77.7036 | [7 empty] | -98.0183
-19.6008 | [7 empty] | -24.7252
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-86.8379 | [7 empty] | -109.5406
-226.971 | [7 empty] | -286.3099
-411.927 | [7 empty] | -519.6203
-624.1347 | [7 empty] | -787.3071
-838.0285 | [7 empty] | -1057.1209
-1022.4028 | [7 empty] | -1289.6977
-1143.8279 | [7 empty] | -1442.8678
-1170.7712 | [7 empty] | -1476.8552
-1077.9468 | [7 empty] | -1359.763
-850.3506 | [7 empty] | -1072.6645
-486.4428 | [7 empty] | -613.6174
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-1033.8264 | [7 empty] | -1304.1078
-2040.1966 | [7 empty] | -2573.5813
-2937.9006 | [7 empty] | -3705.9792
-3652.5645 | [7 empty] | -4607.4833
-4123.4098 | [7 empty] | -5201.4255
-4308.771 | [7 empty] | -5435.2471
-4189.8494 | [7 empty] | -5285.2349
-3772.3624 | [7 empty] | -4758.6009
-3085.9648 | [7 empty] | -3892.753
-2181.5481 | [7 empty] | -2751.8875
-1126.7297 | [7 empty] | -1421.2995
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-994.1638 | [7 empty] | -1254.0759
-1907.9957 | [7 empty] | -2406.8182
-2684.4954 | [7 empty] | -3386.3243
-3276.1074 | [7 empty] | -4132.6061
-3647.045 | [7 empty] | -4600.5208
-3774.9481 | [7 empty] | -4761.8626
-3651.8969 | [7 empty] | -4606.6412
-3284.7912 | [7 empty] | -4143.5601
-2695.0972 | [7 empty] | -3399.6977
-1917.9468 | [7 empty] | -2419.3708
-1000.5657 | [7 empty] | -1262.1515
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-1145.8691 | [7 empty] | -1445.4427
-2219.2718 | [7 empty] | -2799.4735
-3140.1271 | [7 empty] | -3961.0754
-3839.3824 | [7 empty] | -4843.1425
-4265.0091 | [7 empty] | -5380.0442
-4386.6301 | [7 empty] | -5533.4615
-4198.2949 | [7 empty] | -5295.8883
-3719.0844 | [7 empty] | -4691.3941
-2991.4353 | [7 empty] | -3773.5098
-2077.3087 | [7 empty] | -2620.3959
-1052.5541 | [7 empty] | -1327.7317
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-490.0675 | [7 empty] | -618.1897
-854.5941 | [7 empty] | -1078.0174
-1080.0397 | [7 empty] | -1362.403
-1168.5717 | [7 empty] | -1474.0806
-1136.1252 | [7 empty] | -1433.1514
-1009.0962 | [7 empty] | -1272.9122
-820.1592 | [7 empty] | -1034.5799
-603.768 | [7 empty] | -761.6159
-391.8985 | [7 empty] | -494.3557
-210.5274 | [7 empty] | -265.5672
-77.2166 | [7 empty] | -97.4039
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-1.0934 | [7 empty] | -1.3793
-55.6561 | [7 empty] | -70.2067
-124.0295 | [7 empty] | -156.4555
-189.1076 | [7 empty] | -238.5475
-236.5926 | [7 empty] | -298.4469
-256.9183 | [7 empty] | -324.0864
-246.2851 | [7 empty] | -310.6733
-206.7283 | [7 empty] | -260.7749
-145.2783 | [7 empty] | -183.2595
-72.4023 | [7 empty] | -91.3309
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-19.2277 | [7 empty] | -24.2546
-59.3215 | [7 empty] | -74.8304
-82.1001 | [7 empty] | -103.5641
-80.8894 | [7 empty] | -102.037
-52.9626 | [7 empty] | -66.809
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-60.3039 | [7 empty] | -76.0697
-96.8472 | [7 empty] | -122.1667
-107.0424 | [7 empty] | -135.0274
-92.5952 | [7 empty] | -116.8031
-59.159 | [7 empty] | -74.6254
-15.3472 | [7 empty] | -19.3596
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-58.1604 | [7 empty] | -73.3658
-117.5614 | [7 empty] | -148.2964
-167.4487 | [7 empty] | -211.2262
-198.3253 | [7 empty] | -250.175
-203.8608 | [7 empty] | -257.1578
-182.3846 | [7 empty] | -230.0669
-137.6949 | [7 empty] | -173.6935
-78.9997 | [7 empty] | -99.6532
-19.9259 | [7 empty] | -25.1353
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-88.2474 | [7 empty] | -111.3187
-230.6353 | [7 empty] | -290.932
-418.5404 | [7 empty] | -527.9627
-634.0992 | [7 empty] | -799.8768
-851.3331 | [7 empty] | -1073.9039
-1038.5432 | [7 empty] | -1310.0578
-1161.783 | [7 empty] | -1465.5171
-1189.0446 | [7 empty] | -1499.906
-1094.6751 | [7 empty] | -1380.8647
-863.4709 | [7 empty] | -1089.215
-493.9048 | [7 empty] | -623.0302
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-1048.3958 | [7 empty] | -1322.4863
-2068.7672 | [7 empty] | -2609.6214
-2978.7814 | [7 empty] | -3757.5478
-3703.0652 | [7 empty] | -4671.1868
-4180.0541 | [7 empty] | -5272.8787
-4367.5788 | [7 empty] | -5509.4295
-4246.662 | [7 empty] | -5356.9005
-3823.1791 | [7 empty] | -4822.703
-3127.2612 | [7 empty] | -3944.8458
-2210.548 | [7 empty] | -2788.469
-1141.6075 | [7 empty] | -1440.067
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-1006.0584 | [7 empty] | -1269.0803
-1930.6554 | [7 empty] | -2435.4019
-2716.1396 | [7 empty] | -3426.2414
-3314.4359 | [7 empty] | -4180.9551
-3689.391 | [7 empty] | -4653.9377
-3818.4458 | [7 empty] | -4816.7322
-3693.6542 | [7 empty] | -4659.3154
-3322.0608 | [7 empty] | -4190.5734
-2725.4381 | [7 empty] | -3437.9709
-1939.3694 | [7 empty] | -2446.3941
-1011.6532 | [7 empty] | -1276.1377
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-1157.1536 | [7 empty] | -1459.6774
-2240.932 | [7 empty] | -2826.7966
-3170.4989 | [7 empty] | -3999.3874
-3876.1799 | [7 empty] | -4889.5602
-4305.511 | [7 empty] | -5431.1348
-4427.9014 | [7 empty] | -5585.5227
-4237.4254 | [7 empty] | -5345.2491
-3753.4217 | [7 empty] | -4734.7084
-3018.7916 | [7 empty] | -3808.0181
-2096.123 | [7 empty] | -2644.129
-1061.9947 | [7 empty] | -1339.6404
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-493.8615 | [7 empty] | -622.9756
-861.1353 | [7 empty] | -1086.2688
-1088.212 | [7 empty] | -1372.7119
-1177.3116 | [7 empty] | -1485.1055
-1144.5231 | [7 empty] | -1443.7448
-1016.4668 | [7 empty] | -1282.2098
-826.078 | [7 empty] | -1042.0461
-608.0724 | [7 empty] | -767.0456
-394.6582 | [7 empty] | -497.8368
-211.9914 | [7 empty] | -267.414
-77.7468 | [7 empty] | -98.0727
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-1.1006 | [7 empty] | -1.3883
-56.0188 | [7 empty] | -70.6642
-124.827 | [7 empty] | -157.4615
-190.307 | [7 empty] | -240.0604
-238.0726 | [7 empty] | -300.3138
-258.5029 | [7 empty] | -326.0854
-247.7827 | [7 empty] | -312.5624
-207.9673 | [7 empty] | -262.3379
-146.1363 | [7 empty] | -184.3418
-72.8235 | [7 empty] | -91.8623
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-19.3262 | [7 empty] | -24.3787
-59.6201 | [7 empty] | -75.2071
-82.5062 | [7 empty] | -104.0764
-81.2825 | [7 empty] | -102.5329
-53.2153 | [7 empty] | -67.1278
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-60.5183 | [7 empty] | -76.3401
-97.183 | [7 empty] | -122.5904
-107.4044 | [7 empty] | -135.4839
-92.9002 | [7 empty] | -117.1879
-59.3488 | [7 empty] | -74.8648
-15.3951 | [7 empty] | -19.4199
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-58.3066 | [7 empty] | -73.5501
-117.8466 | [7 empty] | -148.6562
-167.8405 | [7 empty] | -211.7203
-198.772 | [7 empty] | -250.7386
-204.3024 | [7 empty] | -257.7147
-182.7638 | [7 empty] | -230.5452
-137.9692 | [7 empty] | -174.0396
-79.1502 | [7 empty] | -99.8431
-19.9621 | [7 empty] | -25.181
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-88.3773 | [7 empty] | -111.4825
-230.9548 | [7 empty] | -291.3351
-419.084 | [7 empty] | -528.6484
-634.8679 | [7 empty] | -800.8465
-852.2914 | [7 empty] | -1075.1127
-1039.6222 | [7 empty] | -1311.4189
-1162.8894 | [7 empty] | -1466.9127
-1190.074 | [7 empty] | -1501.2045
-1095.528 | [7 empty] | -1381.9406
-864.0689 | [7 empty] | -1089.9693
-494.2041 | [7 empty] | -623.4077
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-1047.761 | [7 empty] | -1321.6854
-2067.3355 | [7 empty] | -2607.8154
-2976.4624 | [7 empty] | -3754.6225
-3699.8621 | [7 empty] | -4667.1463
-4176.077 | [7 empty] | -5267.8618
-4363.0457 | [7 empty] | -5503.7113
-4241.8873 | [7 empty] | -5350.8775
-3818.5501 | [7 empty] | -4816.8638
-3123.2045 | [7 empty] | -3939.7285
-2207.4893 | [7 empty] | -2784.6107
-1139.9293 | [7 empty] | -1437.95
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-1003.3628 | [7 empty] | -1265.6799
-1925.3157 | [7 empty] | -2428.6662
-2708.393 | [7 empty] | -3416.4696
-3304.6968 | [7 empty] | -4168.6698
-3678.2316 | [7 empty] | -4639.8607
-3806.5663 | [7 empty] | -4801.7471
-3681.8441 | [7 empty] | -4644.4178
-3311.1521 | [7 empty] | -4176.8128
-2716.2533 | [7 empty] | -3426.3849
-1932.6664 | [7 empty] | -2437.9386
-1008.0694 | [7 empty] | -1271.6169
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-1151.6566 | [7 empty] | -1452.7432
-2230.0931 | [7 empty] | -2813.124
-3154.8904 | [7 empty] | -3979.6984
-3856.763 | [7 empty] | -4865.0671
-4283.5722 | [7 empty] | -5403.4603
-4404.9571 | [7 empty] | -5556.5798
-4215.1026 | [7 empty] | -5317.0902
-3733.3249 | [7 empty] | -4709.3575
-3002.3679 | [7 empty] | -3787.3006
-2084.5383 | [7 empty] | -2629.5156
-1056.0338 | [7 empty] | -1332.121
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-490.4933 | [7 empty] | -618.7269
-855.1881 | [7 empty] | -1078.7666
-1080.6026 | [7 empty] | -1363.1131
-1168.9777 | [7 empty] | -1474.5928
-1136.3226 | [7 empty] | -1433.4004
-1009.0962 | [7 empty] | -1272.9122
-820.0168 | [7 empty] | -1034.4002
-603.5583 | [7 empty] | -761.3514
-391.6944 | [7 empty] | -494.0981
-210.3812 | [7 empty] | -265.3828
-77.1496 | [7 empty] | -97.3194
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-1.0919 | [7 empty] | -1.3774
-55.5692 | [7 empty] | -70.0971
-123.8143 | [7 empty] | -156.184
-188.7466 | [7 empty] | -238.0921
-236.1 | [7 empty] | -297.8255
-256.3388 | [7 empty] | -323.3554
-245.6869 | [7 empty] | -309.9188
-206.1904 | [7 empty] | -260.0964
-144.8751 | [7 empty] | -182.7509
-72.1888 | [7 empty] | -91.0617
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-19.1444 | [7 empty] | -24.1495
-59.0542 | [7 empty] | -74.4933
-81.7159 | [7 empty] | -103.0795
-80.497 | [7 empty] | -101.5419
-52.6965 | [7 empty] | -66.4733
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-59.8551 | [7 empty] | -75.5035
-96.1096 | [7 empty] | -121.2363
-106.2088 | [7 empty] | -133.9758
-91.8581 | [7 empty] | -115.8733
-58.6779 | [7 empty] | -74.0186
-15.2198 | [7 empty] | -19.1989
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-57.6073 | [7 empty] | -72.668
-116.4229 | [7 empty] | -146.8603
-165.7982 | [7 empty] | -209.1441
-196.3362 | [7 empty] | -247.6659
-201.7811 | [7 empty] | -254.5344
-180.4926 | [7 empty] | -227.6802
-136.2428 | [7 empty] | -171.8618
-78.153 | [7 empty] | -98.5852
-19.709 | [7 empty] | -24.8617
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-87.2257 | [7 empty] | -110.0298
-227.9251 | [7 empty] | -287.5133
-413.55 | [7 empty] | -521.6676
-626.4295 | [7 empty] | -790.202
-840.8894 | [7 empty] | -1060.7298
-1025.6242 | [7 empty] | -1293.7612
-1147.1311 | [7 empty] | -1447.0346
-1173.8444 | [7 empty] | -1480.7319
-1080.4931 | [7 empty] | -1362.9749
-852.1358 | [7 empty] | -1074.9164
-487.3363 | [7 empty] | -614.7444
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-1031.9311 | [7 empty] | -1301.717
-2035.9224 | [7 empty] | -2568.1897
-2930.9772 | [7 empty] | -3697.2457
-3643.0017 | [7 empty] | -4595.4205
-4111.5363 | [7 empty] | -5186.4477
-4295.2375 | [7 empty] | -5418.1754
-4175.5946 | [7 empty] | -5267.2533
-3758.5424 | [7 empty] | -4741.1679
-3073.8534 | [7 empty] | -3877.4752
-2172.4167 | [7 empty] | -2740.3687
-1121.7193 | [7 empty] | -1414.9793
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-986.116 | [7 empty] | -1243.9242
-1892.0542 | [7 empty] | -2386.7088
-2661.3679 | [7 empty] | -3357.1503
-3247.0312 | [7 empty] | -4095.9282
-3613.7285 | [7 empty] | -4558.4942
-3739.4821 | [7 empty] | -4717.1245
-3616.6381 | [7 empty] | -4562.1644
-3252.2235 | [7 empty] | -4102.478
-2667.6761 | [7 empty] | -3365.1078
-1897.9349 | [7 empty] | -2394.127
-989.866 | [7 empty] | -1248.6545
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-1129.4577 | [7 empty] | -1424.7407
-2186.9124 | [7 empty] | -2758.6542
-3093.5281 | [7 empty] | -3902.2937
-3781.4134 | [7 empty] | -4770.0182
-4199.5107 | [7 empty] | -5297.422
-4318.1297 | [7 empty] | -5447.0525
-4131.6501 | [7 empty] | -5211.8201
-3659.0855 | [7 empty] | -4615.7092
-2942.4023 | [7 empty] | -3711.6578
-2042.7226 | [7 empty] | -2576.7677
-1034.7578 | [7 empty] | -1305.2828
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-480.0119 | [7 empty] | -605.5052
-836.8385 | [7 empty] | -1055.6198
-1057.3219 | [7 empty] | -1333.7459
-1143.6908 | [7 empty] | -1442.6949
-1111.6426 | [7 empty] | -1402.2682
-987.0913 | [7 empty] | -1245.1543
-802.0633 | [7 empty] | -1011.753
-590.2912 | [7 empty] | -744.6158
-383.0502 | [7 empty] | -483.194
-205.72 | [7 empty] | -259.503
-75.4336 | [7 empty] | -95.1548
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-1.0676 | [7 empty] | -1.3467
-54.3138 | [7 empty] | -68.5135
-121.0061 | [7 empty] | -152.6417
-184.4491 | [7 empty] | -232.671
-230.7035 | [7 empty] | -291.0182
-250.4572 | [7 empty] | -315.9362
-240.0282 | [7 empty] | -302.7807
-201.4233 | [7 empty] | -254.083
-141.513 | [7 empty] | -178.5098
-70.5073 | [7 empty] | -88.9406
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-18.6852 | [7 empty] | -23.5703
-57.6321 | [7 empty] | -72.6993
-79.7407 | [7 empty] | -100.5879
-78.5442 | [7 empty] | -99.0786
-51.4135 | [7 empty] | -64.855
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-58.3241 | [7 empty] | -73.5722
-93.6426 | [7 empty] | -118.1243
-103.4731 | [7 empty] | -130.5249
-89.4839 | [7 empty] | -112.8784
-57.1562 | [7 empty] | -72.0991
-14.824 | [7 empty] | -18.6995
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-56.0726 | [7 empty] | -70.7321
-113.3109 | [7 empty] | -142.9347
-161.3516 | [7 empty] | -203.535
-191.0532 | [7 empty] | -241.0017
-196.3337 | [7 empty] | -247.6628
-175.6039 | [7 empty] | -221.5135
-132.5406 | [7 empty] | -167.1918
-76.0226 | [7 empty] | -95.8977
-19.1702 | [7 empty] | -24.182
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-84.8092 | [7 empty] | -106.9815
-221.59 | [7 empty] | -279.522
-402.0186 | [7 empty] | -507.1215
-608.9065 | [7 empty] | -768.0977
-817.2925 | [7 empty] | -1030.9637
-996.7521 | [7 empty] | -1257.3409
-1114.7366 | [7 empty] | -1406.1709
-1140.5912 | [7 empty] | -1438.785
-1049.7884 | [7 empty] | -1324.2429
-827.8447 | [7 empty] | -1044.2747
-473.401 | [7 empty] | -597.1659
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-1001.1356 | [7 empty] | -1262.8704
-1974.9833 | [7 empty] | -2491.3188
-2842.9855 | [7 empty] | -3586.2497
-3533.3087 | [7 empty] | -4457.0495
-3987.368 | [7 empty] | -5029.8171
-4165.1375 | [7 empty] | -5254.0623
-4048.7452 | [7 empty] | -5107.2407
-3644.0265 | [7 empty] | -4596.7132
-2979.9238 | [7 empty] | -3758.9889
-2105.8385 | [7 empty] | -2656.3845
-1087.2417 | [7 empty] | -1371.4879
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-954.5682 | [7 empty] | -1204.1285
-1831.3532 | [7 empty] | -2310.1383
-2575.7463 | [7 empty] | -3249.144
-3142.2755 | [7 empty] | -3963.7855
-3496.8173 | [7 empty] | -4411.0179
-3618.166 | [7 empty] | -4564.0918
-3498.9817 | [7 empty] | -4413.7482
-3146.1294 | [7 empty] | -3968.6469
-2580.4109 | [7 empty] | -3255.0282
-1835.6786 | [7 empty] | -2315.5945
-957.3073 | [7 empty] | -1207.5837
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-1090.879 | [7 empty] | -1376.0761
-2112.0159 | [7 empty] | -2664.177
-2987.302 | [7 empty] | -3768.2959
-3651.2237 | [7 empty] | -4605.792
-4054.5458 | [7 empty] | -5114.5578
-4168.6785 | [7 empty] | -5258.5291
-3988.2783 | [7 empty] | -5030.9655
-3531.7801 | [7 empty] | -4455.1214
-2839.7645 | [7 empty] | -3582.1866
-1971.2824 | [7 empty] | -2486.6503
-998.4754 | [7 empty] | -1259.5147
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-462.5692 | [7 empty] | -583.5024
-806.3528 | [7 empty] | -1017.164
-1018.7075 | [7 empty] | -1285.0362
-1101.8175 | [7 empty] | -1389.8744
-1070.8412 | [7 empty] | -1350.7997
-950.7711 | [7 empty] | -1199.3387
-772.478 | [7 empty] | -974.433
-568.4636 | [7 empty] | -717.0815
-368.8509 | [7 empty] | -465.2825
-198.0755 | [7 empty] | -249.86
-72.6239 | [7 empty] | -91.6105
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-1.0279 | [7 empty] | -1.2966
-52.2709 | [7 empty] | -65.9365
-116.4432 | [7 empty] | -146.8858
-177.4767 | [7 empty] | -223.8758
-221.9614 | [7 empty] | -279.9905
-240.9435 | [7 empty] | -303.9353
-230.8886 | [7 empty] | -291.2517
-193.7353 | [7 empty] | -244.385
-136.0987 | [7 empty] | -171.6801
-67.8034 | [7 empty] | -85.5298
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-17.9552 | [7 empty] | -22.6494
-55.3742 | [7 empty] | -69.8511
-76.6092 | [7 empty] | -96.6377
-75.4524 | [7 empty] | -95.1785
-49.3851 | [7 empty] | -62.2962
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-55.9473 | [7 empty] | -70.574
-89.8176 | [7 empty] | -113.2993
-99.2369 | [7 empty] | -125.1811
-85.8122 | [7 empty] | -108.2468
-54.8058 | [7 empty] | -69.1341
-14.2133 | [7 empty] | -17.9292
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-53.725 | [7 empty] | -67.7707
-108.5557 | [7 empty] | -136.9363
-154.5651 | [7 empty] | -194.9743
-182.9995 | [7 empty] | -230.8425
-188.0391 | [7 empty] | -237.1996
-168.1687 | [7 empty] | -212.1344
-126.9164 | [7 empty] | -160.0972
-72.7897 | [7 empty] | -91.8197
-18.3535 | [7 empty] | -23.1518
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-81.1629 | [7 empty] | -102.382
-212.0414 | [7 empty] | -267.477
-384.657 | [7 empty] | -485.221
-582.5528 | [7 empty] | -734.8542
-781.8429 | [7 empty] | -986.2463
-953.4248 | [7 empty] | -1202.6862
-1066.1757 | [7 empty] | -1344.9144
-1090.7967 | [7 empty] | -1375.9723
-1003.8592 | [7 empty] | -1266.3061
-791.5479 | [7 empty] | -998.4885
-452.6003 | [7 empty] | -570.9272
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-955.8213 | [7 empty] | -1205.7093
-1885.402 | [7 empty] | -2378.3176
-2713.7634 | [7 empty] | -3423.244
-3372.3737 | [7 empty] | -4254.0401
-3805.3727 | [7 empty] | -4800.2414
-3974.6325 | [7 empty] | -5013.7521
-3863.1788 | [7 empty] | -4873.1602
-3476.663 | [7 empty] | -4385.5945
-2842.7778 | [7 empty] | -3585.9877
-2008.7205 | [7 empty] | -2533.8762
-1036.9965 | [7 empty] | -1308.1066
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-909.1768 | [7 empty] | -1146.8701
-1744.093 | [7 empty] | -2200.065
-2452.7699 | [7 empty] | -3094.017
-2991.949 | [7 empty] | -3774.1579
-3329.1935 | [7 empty] | -4199.5709
-3444.3774 | [7 empty] | -4344.8682
-3330.5813 | [7 empty] | -4201.3216
-2994.4086 | [7 empty] | -3777.2605
-2455.7234 | [7 empty] | -3097.7425
-1746.8004 | [7 empty] | -2203.4803
-910.8653 | [7 empty] | -1149
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-1036.4798 | [7 empty] | -1307.4549
-2006.49 | [7 empty] | -2531.0626
-2837.7524 | [7 empty] | -3579.6485
-3468.0822 | [7 empty] | -4374.7703
-3850.7797 | [7 empty] | -4857.5195
-3958.771 | [7 empty] | -4993.7439
-3787.0665 | [7 empty] | -4777.1492
-3353.2551 | [7 empty] | -4229.9231
-2695.943 | [7 empty] | -3400.7647
-1871.2536 | [7 empty] | -2360.4703
-947.7126 | [7 empty] | -1195.4807
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-438.4183 | [7 empty] | -553.0374
-764.1731 | [7 empty] | -963.9569
-965.3193 | [7 empty] | -1217.6903
-1043.9653 | [7 empty] | -1316.8973
-1014.5099 | [7 empty] | -1279.7413
-900.6625 | [7 empty] | -1136.1298
-731.69 | [7 empty] | -922.9814
-538.3919 | [7 empty] | -679.1479
-349.3025 | [7 empty] | -440.6234
-187.5586 | [7 empty] | -236.5935
-68.761 | [7 empty] | -86.7378
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.97342 | [7 empty] | -1.2279
-49.4701 | [7 empty] | -62.4035
-110.1917 | [7 empty] | -138.9999
-167.9306 | [7 empty] | -211.834
-210.0004 | [7 empty] | -264.9025
-227.9357 | [7 empty] | -287.5267
-218.4007 | [7 empty] | -275.4989
-183.2377 | [7 empty] | -231.143
-128.7108 | [7 empty] | -162.3607
-64.1163 | [7 empty] | -80.8788
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-16.9649 | [7 empty] | -21.4002
-52.3134 | [7 empty] | -65.9901
-72.3668 | [7 empty] | -91.2862
-71.2665 | [7 empty] | -89.8983
-46.6406 | [7 empty] | -58.8342
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-52.7593 | [7 empty] | -66.5525
-84.6901 | [7 empty] | -106.8313
-93.5616 | [7 empty] | -118.0222
-80.8961 | [7 empty] | -102.0454
-51.6607 | [7 empty] | -65.1668
-13.3966 | [7 empty] | -16.899
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-50.5983 | [7 empty] | -63.8266
-102.2264 | [7 empty] | -128.9522
-145.5372 | [7 empty] | -183.5861
-172.292 | [7 empty] | -217.3357
-177.0175 | [7 empty] | -223.2966
-158.2947 | [7 empty] | -199.679
-119.4518 | [7 empty] | -150.681
-68.5014 | [7 empty] | -86.4102
-17.2708 | [7 empty] | -21.786
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-76.3397 | [7 empty] | -96.2978
-199.4178 | [7 empty] | -251.5532
-361.7171 | [7 empty] | -456.2837
-547.7509 | [7 empty] | -690.9537
-735.0547 | [7 empty] | -927.2259
-896.2705 | [7 empty] | -1130.5896
-1002.1527 | [7 empty] | -1264.1534
-1025.183 | [7 empty] | -1293.2047
-943.3717 | [7 empty] | -1190.0048
-743.7717 | [7 empty] | -938.2219
-425.2359 | [7 empty] | -536.4087
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-896.6453 | [7 empty] | -1131.0624
-1768.4778 | [7 empty] | -2230.8249
-2545.1849 | [7 empty] | -3210.5928
-3162.5309 | [7 empty] | -3989.3364
-3568.19 | [7 empty] | -4501.0502
-3726.4853 | [7 empty] | -4700.7298
-3621.5866 | [7 empty] | -4568.4066
-3258.8792 | [7 empty] | -4110.8737
-2664.4045 | [7 empty] | -3360.9808
-1882.471 | [7 empty] | -2374.6203
-971.7122 | [7 empty] | -1225.7547
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-850.6002 | [7 empty] | -1072.9793
-1631.5392 | [7 empty] | -2058.0854
-2294.2223 | [7 empty] | -2894.019
-2798.2317 | [7 empty] | -3529.7955
-3113.288 | [7 empty] | -3927.2195
-3220.6367 | [7 empty] | -4062.6332
-3113.8791 | [7 empty] | -3927.9652
-2799.2613 | [7 empty] | -3531.0943
-2295.4216 | [7 empty] | -2895.5319
-1632.5893 | [7 empty] | -2059.4101
-851.2135 | [7 empty] | -1073.753
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-967.0492 | [7 empty] | -1219.8726
-1871.865 | [7 empty] | -2361.2415
-2647.0483 | [7 empty] | -3339.0871
-3234.6447 | [7 empty] | -4080.3034
-3591.1677 | [7 empty] | -4530.035
-3691.4514 | [7 empty] | -4656.5367
-3530.9326 | [7 empty] | -4454.0522
-3126.0995 | [7 empty] | -3943.3804
-2513.0236 | [7 empty] | -3170.0232
-1744.0871 | [7 empty] | -2200.0576
-883.2058 | [7 empty] | -1114.1093
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-407.9093 | [7 empty] | -514.5522
-710.9111 | [7 empty] | -896.7702
-897.9317 | [7 empty] | -1132.685
-970.973 | [7 empty] | -1224.8221
-943.4659 | [7 empty] | -1190.1236
-837.4921 | [7 empty] | -1056.4443
-680.2907 | [7 empty] | -858.1445
-500.5123 | [7 empty] | -631.3652
-324.6885 | [7 empty] | -409.5743
-174.3217 | [7 empty] | -219.896
-63.9011 | [7 empty] | -80.6073
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.905 | [7 empty] | -1.1416
-45.952 | [7 empty] | -57.9656
-102.3422 | [7 empty] | -129.0984
-155.9492 | [7 empty] | -196.7202
-194.994 | [7 empty] | -245.9728
-211.6223 | [7 empty] | -266.9484
-202.7456 | [7 empty] | -255.7509
-170.0828 | [7 empty] | -214.5489
-119.4564 | [7 empty] | -150.6869
-59.4996 | [7 empty] | -75.055
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-15.7287 | [7 empty] | -19.8408
-48.4941 | [7 empty] | -61.1723
-67.075 | [7 empty] | -84.611
-66.0472 | [7 empty] | -83.3145
-43.2198 | [7 empty] | -54.5192
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-48.8063 | [7 empty] | -61.5661
-78.3346 | [7 empty] | -98.8142
-86.5296 | [7 empty] | -109.1518
-74.8069 | [7 empty] | -94.3643
-47.7665 | [7 empty] | -60.2545
-12.3858 | [7 empty] | -15.6239
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-46.7379 | [7 empty] | -58.957
-94.4146 | [7 empty] | -119.0982
-134.3988 | [7 empty] | -169.5357
-159.086 | [7 empty] | -200.6771
-163.4289 | [7 empty] | -206.1555
-146.1253 | [7 empty] | -184.3279
-110.2549 | [7 empty] | -139.0797
-63.2197 | [7 empty] | -79.7478
-15.9377 | [7 empty] | -20.1045
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-70.4095 | [7 empty] | -88.8172
-183.9023 | [7 empty] | -231.9814
-333.5315 | [7 empty] | -420.7293
-505.0052 | [7 empty] | -637.0327
-677.6066 | [7 empty] | -854.7586
-826.1181 | [7 empty] | -1042.0967
-923.596 | [7 empty] | -1165.059
-944.7016 | [7 empty] | -1191.6825
-869.203 | [7 empty] | -1096.4456
-685.2092 | [7 empty] | -864.3488
-391.7047 | [7 empty] | -494.1111
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-824.4658 | [7 empty] | -1040.0124
-1625.9062 | [7 empty] | -2050.9797
-2339.6949 | [7 empty] | -2951.3799
-2906.8235 | [7 empty] | -3666.7773
-3279.2596 | [7 empty] | -4136.5824
-3424.2947 | [7 empty] | -4319.5351
-3327.4722 | [7 empty] | -4197.3996
-2993.8334 | [7 empty] | -3776.5349
-2447.3906 | [7 empty] | -3087.2312
-1728.921 | [7 empty] | -2180.9265
-892.3359 | [7 empty] | -1125.6263
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-779.6879 | [7 empty] | -983.5278
-1495.324 | [7 empty] | -1886.2584
-2102.4027 | [7 empty] | -2652.0505
-2563.933 | [7 empty] | -3234.2423
-2852.232 | [7 empty] | -3597.9136
-2950.1886 | [7 empty] | -3721.4797
-2852.0179 | [7 empty] | -3597.6435
-2563.5177 | [7 empty] | -3233.7185
-2101.8306 | [7 empty] | -2651.3288
-1494.7017 | [7 empty] | -1885.4734
-779.2172 | [7 empty] | -982.9341
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-883.5941 | [7 empty] | -1114.5991
-1710.0933 | [7 empty] | -2157.1765
-2417.9554 | [7 empty] | -3050.1007
-2954.2967 | [7 empty] | -3726.6619
-3279.4746 | [7 empty] | -4136.8536
-3370.5964 | [7 empty] | -4251.7981
-3223.5913 | [7 empty] | -4066.3603
-2853.6075 | [7 empty] | -3599.6487
-2293.6591 | [7 empty] | -2893.3085
-1591.627 | [7 empty] | -2007.7386
-805.8904 | [7 empty] | -1016.5806
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-371.4847 | [7 empty] | -468.6049
-647.3392 | [7 empty] | -816.5781
-817.5219 | [7 empty] | -1031.2531
-883.8992 | [7 empty] | -1114.984
-858.7393 | [7 empty] | -1083.2463
-762.1761 | [7 empty] | -961.4379
-619.0256 | [7 empty] | -780.8624
-455.3741 | [7 empty] | -574.4262
-295.3658 | [7 empty] | -372.5856
-158.5569 | [7 empty] | -200.0096
-58.1146 | [7 empty] | -73.308
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.8236 | [7 empty] | -1.0389
-41.7676 | [7 empty] | -52.6873
-93.0087 | [7 empty] | -117.3247
-141.7063 | [7 empty] | -178.7537
-177.1599 | [7 empty] | -223.4762
-192.24 | [7 empty] | -242.4989
-184.1503 | [7 empty] | -232.2941
-154.4615 | [7 empty] | -194.8436
-108.4697 | [7 empty] | -136.8279
-54.02 | [7 empty] | -68.1429
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-14.2646 | [7 empty] | -17.9939
-43.9717 | [7 empty] | -55.4675
-60.8106 | [7 empty] | -76.7089
-59.8702 | [7 empty] | -75.5226
-39.1724 | [7 empty] | -49.4136
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-44.1456 | [7 empty] | -55.6869
-70.8432 | [7 empty] | -89.3643
-78.2429 | [7 empty] | -98.6985
-67.633 | [7 empty] | -85.3149
-43.1797 | [7 empty] | -54.4686
-11.1955 | [7 empty] | -14.1225
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-42.1999 | [7 empty] | -53.2326
-85.2338 | [7 empty] | -107.5171
-121.3113 | [7 empty] | -153.0267
-143.573 | [7 empty] | -181.1084
-147.4704 | [7 empty] | -186.0247
-131.8367 | [7 empty] | -166.3038
-99.4592 | [7 empty] | -125.4616
-57.0214 | [7 empty] | -71.9289
-14.3737 | [7 empty] | -18.1315
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-63.4583 | [7 empty] | -80.0487
-165.7199 | [7 empty] | -209.0454
-300.509 | [7 empty] | -379.0735
-454.9359 | [7 empty] | -573.8734
-610.3315 | [7 empty] | -769.8953
-743.985 | [7 empty] | -938.4909
-831.645 | [7 empty] | -1049.0686
-850.5199 | [7 empty] | -1072.878
-782.4287 | [7 empty] | -986.9853
-616.7094 | [7 empty] | -777.9407
-352.4929 | [7 empty] | -444.6478
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-740.3296 | [7 empty] | -933.8798
-1459.755 | [7 empty] | -1841.3903
-2100.2735 | [7 empty] | -2649.3647
-2608.9598 | [7 empty] | -3291.0408
-2942.7717 | [7 empty] | -3712.1237
-3072.4432 | [7 empty] | -3875.6963
-2985.1012 | [7 empty] | -3765.5198
-2685.3695 | [7 empty] | -3387.4269
-2194.8834 | [7 empty] | -2768.7091
-1550.2975 | [7 empty] | -1955.604
-800.0185 | [7 empty] | -1009.1736
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-697.4682 | [7 empty] | -879.8128
-1337.423 | [7 empty] | -1687.0761
-1880.0931 | [7 empty] | -2371.6207
-2292.4509 | [7 empty] | -2891.7845
-2549.8115 | [7 empty] | -3216.4289
-2636.9554 | [7 empty] | -3326.3555
-2548.7952 | [7 empty] | -3215.1469
-2290.5968 | [7 empty] | -2889.4456
-1877.7578 | [7 empty] | -2368.6749
-1335.1372 | [7 empty] | -1684.1927
-695.9203 | [7 empty] | -877.8602
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-787.3248 | [7 empty] | -993.1613
-1523.5211 | [7 empty] | -1921.8272
-2153.7962 | [7 empty] | -2716.8801
-2631.1041 | [7 empty] | -3318.9744
-2920.221 | [7 empty] | -3683.6774
-3000.8593 | [7 empty] | -3785.3977
-2869.4999 | [7 empty] | -3619.696
-2539.7311 | [7 empty] | -3203.7131
-2041.0308 | [7 empty] | -2574.6336
-1416.0844 | [7 empty] | -1786.3025
-716.8876 | [7 empty] | -904.3092
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-329.6728 | [7 empty] | -415.8617
-574.3793 | [7 empty] | -724.5438
-725.2561 | [7 empty] | -914.8655
-784.0069 | [7 empty] | -988.976
-761.5589 | [7 empty] | -960.6593
-675.8068 | [7 empty] | -852.4883
-548.7832 | [7 empty] | -692.2559
-403.632 | [7 empty] | -509.1567
-261.7596 | [7 empty] | -330.1935
-140.4927 | [7 empty] | -177.2228
-51.4855 | [7 empty] | -64.9457
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.7304 | [7 empty] | -0.92135
-36.9777 | [7 empty] | -46.645
-82.3265 | [7 empty] | -103.8498
-125.4084 | [7 empty] | -158.195
-156.7566 | [7 empty] | -197.7387
-170.0699 | [7 empty] | -214.5327
-162.8844 | [7 empty] | -205.4686
-136.6002 | [7 empty] | -172.3127
-95.9101 | [7 empty] | -120.9847
-47.7572 | [7 empty] | -60.2428
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-12.5937 | [7 empty] | -15.8862
-38.8117 | [7 empty] | -48.9585
-53.6645 | [7 empty] | -67.6944
-52.8251 | [7 empty] | -66.6356
-34.5571 | [7 empty] | -43.5916
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-38.8448 | [7 empty] | -49.0003
-62.3245 | [7 empty] | -78.6185
-68.8216 | [7 empty] | -86.8141
-59.4784 | [7 empty] | -75.0283
-37.9669 | [7 empty] | -47.8929
-9.843 | [7 empty] | -12.4164
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-37.0501 | [7 empty] | -46.7363
-74.8169 | [7 empty] | -94.3769
-106.4648 | [7 empty] | -134.2987
-125.978 | [7 empty] | -158.9134
-129.3732 | [7 empty] | -163.1963
-115.6364 | [7 empty] | -145.8681
-87.2212 | [7 empty] | -110.0242
-49.9962 | [7 empty] | -63.0671
-12.6014 | [7 empty] | -15.8958
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-55.587 | [7 empty] | -70.1195
-145.1343 | [7 empty] | -183.0779
-263.1285 | [7 empty] | -331.9203
-398.2689 | [7 empty] | -502.3915
-534.2052 | [7 empty] | -673.8667
-651.0625 | [7 empty] | -821.2749
-727.6332 | [7 empty] | -917.8641
-744.0035 | [7 empty] | -938.5142
-684.3075 | [7 empty] | -863.2114
-539.266 | [7 empty] | -680.2506
-308.1691 | [7 empty] | -388.7362
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-645.4569 | [7 empty] | -814.2037
-1272.4338 | [7 empty] | -1605.0962
-1830.3929 | [7 empty] | -2308.927
-2273.2597 | [7 empty] | -2867.5759
-2563.6062 | [7 empty] | -3233.83
-2676.0336 | [7 empty] | -3375.6502
-2599.4387 | [7 empty] | -3279.0305
-2337.9611 | [7 empty] | -2949.1928
-1910.545 | [7 empty] | -2410.0338
-1349.1907 | [7 empty] | -1701.9203
-696.0989 | [7 empty] | -878.0856
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-605.1336 | [7 empty] | -763.3384
-1160.1261 | [7 empty] | -1463.427
-1630.5175 | [7 empty] | -2056.7965
-1987.7225 | [7 empty] | -2507.3886
-2210.4124 | [7 empty] | -2788.2979
-2285.4798 | [7 empty] | -2882.9908
-2208.6087 | [7 empty] | -2786.0227
-1984.4564 | [7 empty] | -2503.2686
-1626.4528 | [7 empty] | -2051.6693
-1156.2099 | [7 empty] | -1458.487
-602.531 | [7 empty] | -760.0554
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-679.6373 | [7 empty] | -857.3203
-1314.854 | [7 empty] | -1658.6067
-1858.4015 | [7 empty] | -2344.2581
-2269.7538 | [7 empty] | -2863.1535
-2518.6168 | [7 empty] | -3177.0787
-2587.6023 | [7 empty] | -3264.0996
-2473.7935 | [7 empty] | -3120.5369
-2189.0223 | [7 empty] | -2761.3157
-1758.8025 | [7 empty] | -2218.6201
-1220.005 | [7 empty] | -1538.9606
-617.4883 | [7 empty] | -778.9231
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-283.0799 | [7 empty] | -357.0877
-493.0896 | [7 empty] | -622.002
-622.4724 | [7 empty] | -785.2102
-672.7445 | [7 empty] | -848.6255
-653.3341 | [7 empty] | -824.1404
-579.6367 | [7 empty] | -731.1757
-470.5822 | [7 empty] | -593.6102
-346.0363 | [7 empty] | -436.5034
-224.3575 | [7 empty] | -283.013
-120.3912 | [7 empty] | -151.866
-44.1098 | [7 empty] | -55.6417
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.62675 | [7 empty] | -0.7906
-31.6516 | [7 empty] | -39.9265
-70.4505 | [7 empty] | -88.8689
-107.292 | [7 empty] | -135.3422
-134.0801 | [7 empty] | -169.1337
-145.4335 | [7 empty] | -183.4554
-139.2565 | [7 empty] | -175.6634
-116.758 | [7 empty] | -147.283
-81.9597 | [7 empty] | -103.3871
-40.802 | [7 empty] | -51.4691
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-10.7403 | [7 empty] | -13.5483
-33.0889 | [7 empty] | -41.7396
-45.7402 | [7 empty] | -57.6985
-45.014 | [7 empty] | -56.7824
-29.4407 | [7 empty] | -37.1376
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-32.9809 | [7 empty] | -41.6033
-52.9021 | [7 empty] | -66.7327
-58.4023 | [7 empty] | -73.6709
-50.4614 | [7 empty] | -63.6539
-32.2036 | [7 empty] | -40.6228
-8.3479 | [7 empty] | -10.5304
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-31.363 | [7 empty] | -39.5625
-63.3152 | [7 empty] | -79.8682
-90.0743 | [7 empty] | -113.6231
-106.556 | [7 empty] | -134.4138
-109.4 | [7 empty] | -138.0013
-97.7591 | [7 empty] | -123.3171
-73.7185 | [7 empty] | -92.9913
-42.2461 | [7 empty] | -53.2909
-10.6464 | [7 empty] | -13.4298
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-46.9096 | [7 empty] | -59.1736
-122.444 | [7 empty] | -154.4555
-221.9321 | [7 empty] | -279.9536
-335.8262 | [7 empty] | -423.6239
-450.3317 | [7 empty] | -568.0655
-548.6979 | [7 empty] | -692.1484
-613.069 | [7 empty] | -773.3485
-626.6973 | [7 empty] | -790.5398
-576.2621 | [7 empty] | -726.9189
-454.002 | [7 empty] | -572.6953
-259.3763 | [7 empty] | -327.1871
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-541.2235 | [7 empty] | -682.7198
-1066.6591 | [7 empty] | -1345.5243
-1533.9671 | [7 empty] | -1935.0043
-1904.5916 | [7 empty] | -2402.5241
-2147.262 | [7 empty] | -2708.6377
-2240.8148 | [7 empty] | -2826.6487
-2176.0779 | [7 empty] | -2744.9871
-1956.6464 | [7 empty] | -2468.1879
-1598.4989 | [7 empty] | -2016.4071
-1128.5174 | [7 empty] | -1423.5547
-582.0843 | [7 empty] | -734.2632
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-504.0231 | [7 empty] | -635.7939
-966.0045 | [7 empty] | -1218.5547
-1357.2953 | [7 empty] | -1712.1437
-1654.1673 | [7 empty] | -2086.6293
-1838.9567 | [7 empty] | -2319.7297
-1900.859 | [7 empty] | -2397.8156
-1836.3918 | [7 empty] | -2316.4942
-1649.5366 | [7 empty] | -2080.7879
-1351.5603 | [7 empty] | -1704.9094
-960.5148 | [7 empty] | -1211.6298
-500.4035 | [7 empty] | -631.228
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-562.0936 | [7 empty] | -709.0461
-1087.1183 | [7 empty] | -1371.3323
-1536.0554 | [7 empty] | -1937.6385
-1875.4865 | [7 empty] | -2365.8098
-2080.4864 | [7 empty] | -2624.4044
-2136.8185 | [7 empty] | -2695.4638
-2042.211 | [7 empty] | -2576.1224
-1806.5672 | [7 empty] | -2278.8723
-1451.0672 | [7 empty] | -1830.4311
-1006.2327 | [7 empty] | -1269.3
-509.1339 | [7 empty] | -642.2408
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-232.3818 | [7 empty] | -293.1352
-404.649 | [7 empty] | -510.4396
-510.6614 | [7 empty] | -644.1676
-551.7258 | [7 empty] | -695.9679
-535.6345 | [7 empty] | -675.6696
-475.0605 | [7 empty] | -599.2593
-385.5567 | [7 empty] | -486.3558
-283.4224 | [7 empty] | -357.5198
-183.7017 | [7 empty] | -231.7283
-98.5438 | [7 empty] | -124.3069
-36.0945 | [7 empty] | -45.531
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.51416 | [7 empty] | -0.64857
-25.8666 | [7 empty] | -32.6291
-57.5529 | [7 empty] | -72.5994
-87.6197 | [7 empty] | -110.5268
-109.4592 | [7 empty] | -138.076
-118.6881 | [7 empty] | -149.7177
-113.6092 | [7 empty] | -143.3109
-95.2227 | [7 empty] | -120.1175
-66.8208 | [7 empty] | -84.2903
-33.2551 | [7 empty] | -41.9493
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-8.7313 | [7 empty] | -11.014
-26.8865 | [7 empty] | -33.9156
-37.1528 | [7 empty] | -46.8659
-36.5503 | [7 empty] | -46.1059
-23.8975 | [7 empty] | -30.1452
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-26.6387 | [7 empty] | -33.6031
-42.7126 | [7 empty] | -53.8793
-47.1362 | [7 empty] | -59.4594
-40.7126 | [7 empty] | -51.3564
-25.9734 | [7 empty] | -32.7638
-6.7319 | [7 empty] | -8.4919
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-25.2212 | [7 empty] | -31.815
-50.8954 | [7 empty] | -64.2014
-72.3777 | [7 empty] | -91.2999
-85.589 | [7 empty] | -107.9652
-87.8403 | [7 empty] | -110.8051
-78.4643 | [7 empty] | -98.9778
-59.1468 | [7 empty] | -74.61
-33.8835 | [7 empty] | -42.7419
-8.5372 | [7 empty] | -10.7692
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-37.5521 | [7 empty] | -47.3697
-97.9781 | [7 empty] | -123.5933
-177.5173 | [7 empty] | -223.927
-268.5133 | [7 empty] | -338.7129
-359.9274 | [7 empty] | -454.0261
-438.376 | [7 empty] | -552.9842
-489.6138 | [7 empty] | -617.6175
-500.3026 | [7 empty] | -631.1007
-459.8596 | [7 empty] | -580.0844
-362.1539 | [7 empty] | -456.8346
-206.822 | [7 empty] | -260.8931
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-429.1411 | [7 empty] | -541.3349
-845.4153 | [7 empty] | -1066.439
-1215.295 | [7 empty] | -1533.0192
-1508.3023 | [7 empty] | -1902.6297
-1699.7772 | [7 empty] | -2144.1633
-1773.0986 | [7 empty] | -2236.6538
-1721.1585 | [7 empty] | -2171.1346
-1546.9555 | [7 empty] | -1951.3883
-1263.2706 | [7 empty] | -1593.5375
-891.4779 | [7 empty] | -1124.544
-459.6281 | [7 empty] | -579.7923
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-395.6032 | [7 empty] | -499.0289
-757.8735 | [7 empty] | -956.0104
-1064.389 | [7 empty] | -1342.6606
-1296.6225 | [7 empty] | -1635.6088
-1440.8317 | [7 empty] | -1817.5197
-1488.671 | [7 empty] | -1877.8661
-1437.5427 | [7 empty] | -1813.3708
-1290.6943 | [7 empty] | -1628.1308
-1057.0668 | [7 empty] | -1333.4242
-750.8899 | [7 empty] | -947.201
-391.0191 | [7 empty] | -493.2463
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-436.3982 | [7 empty] | -550.4892
-843.6168 | [7 empty] | -1064.1702
-1191.4327 | [7 empty] | -1502.9184
-1454.02 | [7 empty] | -1834.1559
-1612.1838 | [7 empty] | -2033.6697
-1655.0455 | [7 empty] | -2087.7372
-1581.0113 | [7 empty] | -1994.3476
-1397.9123 | [7 empty] | -1763.3796
-1122.2878 | [7 empty] | -1415.6964
-777.8675 | [7 empty] | -981.2315
-393.396 | [7 empty] | -496.2446
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-178.3137 | [7 empty] | -224.9317
-310.3402 | [7 empty] | -391.4748
-391.4446 | [7 empty] | -493.7831
-422.7058 | [7 empty] | -533.2172
-410.1669 | [7 empty] | -517.4001
-363.5948 | [7 empty] | -458.6523
-294.9398 | [7 empty] | -372.0482
-216.6983 | [7 empty] | -273.3514
-140.3819 | [7 empty] | -177.0831
-75.2674 | [7 empty] | -94.9452
-27.556 | [7 empty] | -34.7601
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.39425 | [7 empty] | -0.49732
-19.7066 | [7 empty] | -24.8587
-43.8208 | [7 empty] | -55.2772
-66.6768 | [7 empty] | -84.1086
-83.2511 | [7 empty] | -105.016
-90.2216 | [7 empty] | -113.8089
-86.3143 | [7 empty] | -108.8802
-72.3065 | [7 empty] | -91.2102
-50.713 | [7 empty] | -63.9713
-25.2261 | [7 empty] | -31.8212
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-6.5959 | [7 empty] | -8.3203
-20.2942 | [7 empty] | -25.5999
-28.0266 | [7 empty] | -35.3539
-27.5566 | [7 empty] | -34.761
-18.0078 | [7 empty] | -22.7158
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-19.9104 | [7 empty] | -25.1158
-31.9039 | [7 empty] | -40.2447
-35.1867 | [7 empty] | -44.3858
-30.3736 | [7 empty] | -38.3144
-19.3666 | [7 empty] | -24.4298
-5.0184 | [7 empty] | -6.3304
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-18.7139 | [7 empty] | -23.6064
-37.7376 | [7 empty] | -47.6037
-53.6315 | [7 empty] | -67.6528
-63.3807 | [7 empty] | -79.9509
-65.0069 | [7 empty] | -82.0022
-58.0316 | [7 empty] | -73.2033
-43.7174 | [7 empty] | -55.1468
-25.0296 | [7 empty] | -31.5733
-6.3043 | [7 empty] | -7.9525
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-27.6501 | [7 empty] | -34.8789
-72.0915 | [7 empty] | -90.9389
-130.5281 | [7 empty] | -164.6531
-197.3065 | [7 empty] | -248.8898
-264.3034 | [7 empty] | -333.4023
-321.6967 | [7 empty] | -405.8004
-359.0582 | [7 empty] | -452.9296
-366.6523 | [7 empty] | -462.5092
-336.7881 | [7 empty] | -424.8373
-265.0538 | [7 empty] | -334.3489
-151.2684 | [7 empty] | -190.8157
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-310.8353 | [7 empty] | -392.0994
-611.911 | [7 empty] | -771.8878
-878.9981 | [7 empty] | -1108.8016
-1090.1389 | [7 empty] | -1375.1425
-1227.6414 | [7 empty] | -1548.5934
-1279.6681 | [7 empty] | -1614.2219
-1241.278 | [7 empty] | -1565.7952
-1114.8299 | [7 empty] | -1406.2887
-909.7219 | [7 empty] | -1147.5576
-641.5098 | [7 empty] | -809.2248
-330.5063 | [7 empty] | -416.9132
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-281.4462 | [7 empty] | -355.0269
-538.7516 | [7 empty] | -679.6017
-756.0465 | [7 empty] | -953.7057
-920.2735 | [7 empty] | -1160.8679
-1021.8111 | [7 empty] | -1288.9512
-1054.8937 | [7 empty] | -1330.6829
-1017.8457 | [7 empty] | -1283.9491
-913.1339 | [7 empty] | -1151.8617
-747.2433 | [7 empty] | -942.6011
-530.3754 | [7 empty] | -669.0356
-275.9641 | [7 empty] | -348.1115
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-304.374 | [7 empty] | -383.9489
-587.8809 | [7 empty] | -741.5752
-829.5314 | [7 empty] | -1046.4023
-1011.4666 | [7 empty] | -1275.9023
-1120.5005 | [7 empty] | -1413.4418
-1149.2703 | [7 empty] | -1449.7332
-1096.8831 | [7 empty] | -1383.6499
-968.9844 | [7 empty] | -1222.3136
-777.2326 | [7 empty] | -980.4307
-538.2214 | [7 empty] | -678.9329
-271.9529 | [7 empty] | -343.0517
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-121.6598 | [7 empty] | -153.4663
-211.5307 | [7 empty] | -266.8328
-266.551 | [7 empty] | -336.2376
-287.5557 | [7 empty] | -362.7336
-278.751 | [7 empty] | -351.6271
-246.8563 | [7 empty] | -311.3938
-200.0456 | [7 empty] | -252.3451
-146.8316 | [7 empty] | -185.219
-95.0264 | [7 empty] | -119.8699
-50.8996 | [7 empty] | -64.2067
-18.6179 | [7 empty] | -23.4853
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.26877 | [7 empty] | -0.33904
-13.261 | [7 empty] | -16.7279
-29.4533 | [7 empty] | -37.1535
-44.7671 | [7 empty] | -56.4709
-55.8357 | [7 empty] | -70.4333
-60.4467 | [7 empty] | -76.2498
-57.7679 | [7 empty] | -72.8706
-48.3419 | [7 empty] | -60.9803
-33.8699 | [7 empty] | -42.7248
-16.8314 | [7 empty] | -21.2318
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-4.3649 | [7 empty] | -5.506
-13.4078 | [7 empty] | -16.9131
-18.4942 | [7 empty] | -23.3293
-18.1634 | [7 empty] | -22.9121
-11.8572 | [7 empty] | -14.9571
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-12.8935 | [7 empty] | -16.2644
-20.6325 | [7 empty] | -26.0267
-22.727 | [7 empty] | -28.6687
-19.5942 | [7 empty] | -24.7169
-12.4792 | [7 empty] | -15.7417
-3.2322 | [7 empty] | -4.0773
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-11.9352 | [7 empty] | -15.0556
-24.0327 | [7 empty] | -30.3158
-34.1077 | [7 empty] | -43.0248
-40.2535 | [7 empty] | -50.7773
-41.2308 | [7 empty] | -52.0101
-36.7575 | [7 empty] | -46.3674
-27.6542 | [7 empty] | -34.8841
-15.8129 | [7 empty] | -19.947
-3.9802 | [7 empty] | -5.0207
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-17.3473 | [7 empty] | -21.8826
-45.1594 | [7 empty] | -56.9658
-81.6461 | [7 empty] | -102.9915
-123.2383 | [7 empty] | -155.4574
-164.8464 | [7 empty] | -207.9435
-200.3521 | [7 empty] | -252.7317
-223.2954 | [7 empty] | -281.6733
-227.6848 | [7 empty] | -287.2103
-208.8325 | [7 empty] | -263.4293
-164.1099 | [7 empty] | -207.0145
-93.5212 | [7 empty] | -117.9712
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-188.0216 | [7 empty] | -237.1776
-369.5326 | [7 empty] | -466.1424
-529.9537 | [7 empty] | -668.5037
-656.1658 | [7 empty] | -827.7124
-737.7018 | [7 empty] | -930.565
-767.6793 | [7 empty] | -968.3798
-743.396 | [7 empty] | -937.748
-666.5366 | [7 empty] | -840.7945
-542.98 | [7 empty] | -684.9355
-382.2383 | [7 empty] | -482.1699
-196.5914 | [7 empty] | -247.9879
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-163.2076 | [7 empty] | -205.8763
-311.8165 | [7 empty] | -393.3372
-436.7396 | [7 empty] | -550.9198
-530.5784 | [7 empty] | -669.2917
-587.9717 | [7 empty] | -741.6898
-605.8178 | [7 empty] | -764.2016
-583.3675 | [7 empty] | -735.8818
-522.3108 | [7 empty] | -658.8627
-426.5631 | [7 empty] | -538.0828
-302.1491 | [7 empty] | -381.1424
-156.887 | [7 empty] | -197.9032
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
-167.9158 | [7 empty] | -211.8153
-323.5993 | [7 empty] | -408.2004
-455.5798 | [7 empty] | -574.6856
-554.2245 | [7 empty] | -699.1198
-612.5473 | [7 empty] | -772.6904
-626.8079 | [7 empty] | -790.6793
-596.8274 | [7 empty] | -752.8607
-525.9838 | [7 empty] | -663.4959
-420.8857 | [7 empty] | -530.9211
-290.7499 | [7 empty] | -366.7629
-146.546 | [7 empty] | -184.8587
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
-63.2216 | [7 empty] | -79.7501
-109.6336 | [7 empty] | -138.296
-137.7719 | [7 empty] | -173.7908
-148.2154 | [7 empty] | -186.9645
-143.2727 | [7 empty] | -180.7296
-126.5178 | [7 empty] | -159.5943
-102.2304 | [7 empty] | -128.9574
-74.8157 | [7 empty] | -94.3753
-48.2729 | [7 empty] | -60.8933
-25.7738 | [7 empty] | -32.5121
-9.39 | [7 empty] | -11.8449
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
-0.11954 | [7 empty] | -0.1508
-6.6032 | [7 empty] | -8.3295
-14.6388 | [7 empty] | -18.466
-22.1883 | [7 empty] | -27.9891
-27.5907 | [7 empty] | -34.804
-29.7754 | [7 empty] | -37.5598
-28.3638 | [7 empty] | -35.7792
-23.6563 | [7 empty] | -29.841
-16.5157 | [7 empty] | -20.8335
-8.1728 | [7 empty] | -10.3095
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
-2.0508 | [7 empty] | -2.5869
-6.3071 | [7 empty] | -7.956
-8.6737 | [7 empty] | -10.9413
-8.487 | [7 empty] | -10.7058
-5.5147 | [7 empty] | -6.9565
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
-5.6698 | [7 empty] | -7.152
-9.0421 | [7 empty] | -11.4061
-9.9178 | [7 empty] | -12.5107
-8.5108 | [7 empty] | -10.7359
-5.3909 | [7 empty] | -6.8003
-1.3794 | [7 empty] | -1.74
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
-4.9637 | [7 empty] | -6.2614
-9.9594 | [7 empty] | -12.5632
-14.0694 | [7 empty] | -17.7477
-16.5226 | [7 empty] | -20.8423
-16.837 | [7 empty] | -21.2388
-14.9305 | [7 empty] | -18.8339
-11.1701 | [7 empty] | -14.0904
-6.347 | [7 empty] | -8.0064
-1.5784 | [7 empty] | -1.9911
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
-6.7731 | [7 empty] | -8.5438
-17.5526 | [7 empty] | -22.1415
-31.5602 | [7 empty] | -39.8112
-47.363 | [7 empty] | -59.7454
-62.9789 | [7 empty] | -79.444
-76.082 | [7 empty] | -95.9728
-84.2745 | [7 empty] | -106.307
-85.3955 | [7 empty] | -107.7211
-77.8284 | [7 empty] | -98.1757
-60.7661 | [7 empty] | -76.6527
-34.3978 | [7 empty] | -43.3907
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
-62.4614 | [7 empty] | -78.7912
-121.7751 | [7 empty] | -153.6118
-173.2037 | [7 empty] | -218.4857
-212.6568 | [7 empty] | -268.2533
-237.0438 | [7 empty] | -299.016
-244.5373 | [7 empty] | -308.4687
-234.7131 | [7 empty] | -296.0759
-208.5569 | [7 empty] | -263.0816
-168.3436 | [7 empty] | -212.355
-117.4036 | [7 empty] | -148.0973
-59.8057 | [7 empty] | -75.4411
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
-42.5823 | [7 empty] | -53.7149
-80.3395 | [7 empty] | -101.3433
-111.0789 | [7 empty] | -140.1192
-133.1687 | [7 empty] | -167.984
-145.5854 | [7 empty] | -183.6469
-147.9362 | [7 empty] | -186.6123
-140.4488 | [7 empty] | -177.1674
-123.9327 | [7 empty] | -156.3335
-99.7164 | [7 empty] | -125.786
-69.5608 | [7 empty] | -87.7467
-35.5545 | [7 empty] | -44.8498
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
-29.0422 | [7 empty] | -36.635
-54.6445 | [7 empty] | -68.9306
-75.0411 | [7 empty] | -94.6596
-88.9646 | [7 empty] | -112.2233
-95.7304 | [7 empty] | -120.7579
-95.2751 | [7 empty] | -120.1836
-88.136 | [7 empty] | -111.1781
-75.375 | [7 empty] | -95.0809
-58.4546 | [7 empty] | -73.7369
-39.0816 | [7 empty] | -49.299
-19.0337 | [7 empty] | -24.0098
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
-3.8864 | [7 empty] | -4.9024
-6.1665 | [7 empty] | -7.7786
-7.0147 | [7 empty] | -8.8486
-6.7454 | [7 empty] | -8.5089
-5.7364 | [7 empty] | -7.2361
-4.3644 | [7 empty] | -5.5054
-2.9525 | [7 empty] | -3.7244
-1.7346 | [7 empty] | -2.188
-0.8392 | [7 empty] | -1.0586
-0.29409 | [7 empty] | -0.37098
-0.045758 | [7 empty] | -0.057721
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.0084355 | [7 empty] | -0.010641
0.11052 | [7 empty] | 0.078853
0.34811 | [7 empty] | 0.24837
0.67248 | [7 empty] | 0.47979
1.0145 | [7 empty] | 0.72385
1.2879 | [7 empty] | 0.91887
1.4118 | [7 empty] | 1.0073
1.3325 | [7 empty] | 0.9507
1.0382 | [7 empty] | 0.7407
0.56452 | [7 empty] | 0.40277
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
0.25327 | [7 empty] | 0.1807
0.84524 | [7 empty] | 0.60305
1.2328 | [7 empty] | 0.87955
1.2727 | [7 empty] | 0.908
0.86788 | [7 empty] | 0.6192
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
1.5964 | [7 empty] | 1.139
2.6395 | [7 empty] | 1.8832
2.9953 | [7 empty] | 2.1371
2.6561 | [7 empty] | 1.8951
1.7358 | [7 empty] | 1.2384
0.45368 | [7 empty] | 0.32368
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
2.04 | [7 empty] | 1.4555
4.2185 | [7 empty] | 3.0097
6.133 | [7 empty] | 4.3757
7.408 | [7 empty] | 5.2854
7.7612 | [7 empty] | 5.5374
7.0732 | [7 empty] | 5.0465
5.4362 | [7 empty] | 3.8785
3.1711 | [7 empty] | 2.2625
0.80632 | [7 empty] | 0.57529
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
3.8596 | [7 empty] | 2.7537
10.269 | [7 empty] | 7.3266
18.9436 | [7 empty] | 13.5156
29.1594 | [7 empty] | 20.8043
39.7621 | [7 empty] | 28.3689
49.2516 | [7 empty] | 35.1394
55.9289 | [7 empty] | 39.9034
58.0925 | [7 empty] | 41.4471
54.2645 | [7 empty] | 38.7159
43.419 | [7 empty] | 30.9781
25.1845 | [7 empty] | 17.9683
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
63.9649 | [7 empty] | 45.6368
127.7085 | [7 empty] | 91.1158
186.0183 | [7 empty] | 132.7179
233.8965 | [7 empty] | 166.8774
267.0121 | [7 empty] | 190.5043
282.1112 | [7 empty] | 201.2771
277.334 | [7 empty] | 197.8687
252.4075 | [7 empty] | 180.0844
208.6943 | [7 empty] | 148.8965
149.094 | [7 empty] | 106.3737
77.8076 | [7 empty] | 55.5132
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
78.6208 | [7 empty] | 56.0933
152.2628 | [7 empty] | 108.6345
216.1528 | [7 empty] | 154.2179
266.1325 | [7 empty] | 189.8768
298.8724 | [7 empty] | 213.2356
312.051 | [7 empty] | 222.6381
304.4869 | [7 empty] | 217.2414
276.2228 | [7 empty] | 197.0759
228.5566 | [7 empty] | 163.0676
164.0164 | [7 empty] | 117.0203
86.2738 | [7 empty] | 61.5535
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
110.2327 | [7 empty] | 78.6474
215.0829 | [7 empty] | 153.4545
306.5661 | [7 empty] | 218.7248
377.5657 | [7 empty] | 269.3807
422.455 | [7 empty] | 301.4077
437.6197 | [7 empty] | 312.2272
421.8137 | [7 empty] | 300.9502
376.3071 | [7 empty] | 268.4827
304.8042 | [7 empty] | 217.4678
213.1336 | [7 empty] | 152.0638
108.7348 | [7 empty] | 77.5787
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
55.4853 | [7 empty] | 39.5869
97.3703 | [7 empty] | 69.4705
123.8245 | [7 empty] | 88.3447
134.8025 | [7 empty] | 96.1772
131.8633 | [7 empty] | 94.0801
117.8325 | [7 empty] | 84.0696
96.3484 | [7 empty] | 68.7414
71.3519 | [7 empty] | 50.9072
46.5868 | [7 empty] | 33.2382
25.1701 | [7 empty] | 17.958
9.2793 | [7 empty] | 6.6205
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
0.12265 | [7 empty] | 0.087507
6.8425 | [7 empty] | 4.8819
15.3498 | [7 empty] | 10.9516
23.5433 | [7 empty] | 16.7974
29.625 | [7 empty] | 21.1364
32.3524 | [7 empty] | 23.0824
31.1868 | [7 empty] | 22.2507
26.3218 | [7 empty] | 18.7798
18.5968 | [7 empty] | 13.2682
9.3135 | [7 empty] | 6.6449
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
2.5735 | [7 empty] | 1.8361
8.0052 | [7 empty] | 5.7114
11.1412 | [7 empty] | 7.9489
11.0337 | [7 empty] | 7.8722
7.2577 | [7 empty] | 5.1782
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
8.8592 | [7 empty] | 6.3208
14.3028 | [7 empty] | 10.2046
15.8849 | [7 empty] | 11.3333
13.8044 | [7 empty] | 9.849
8.8571 | [7 empty] | 6.3192
2.3 | [7 empty] | 1.641
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
-0.01 | [7 empty] | -0.012614
9.034 | [7 empty] | 6.4455
18.355 | [7 empty] | 13.0957
26.2664 | [7 empty] | 18.7402
31.2511 | [7 empty] | 22.2966
32.2667 | [7 empty] | 23.0212
29.0142 | [7 empty] | 20.7007
22.0035 | [7 empty] | 15.6988
12.683 | [7 empty] | 9.0489
3.2193 | [7 empty] | 2.2968
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
14.4761 | [7 empty] | 10.3282
37.9814 | [7 empty] | 27.0985
69.2125 | [7 empty] | 49.3808
105.2987 | [7 empty] | 75.1272
141.9663 | [7 empty] | 101.2883
173.9108 | [7 empty] | 124.0796
195.3609 | [7 empty] | 139.3836
200.7778 | [7 empty] | 143.2484
185.6103 | [7 empty] | 132.4268
147.0144 | [7 empty] | 104.8899
84.4415 | [7 empty] | 60.2463
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
189.5033 | [7 empty] | 135.2044
375.3799 | [7 empty] | 267.8212
542.5824 | [7 empty] | 387.1147
677.0975 | [7 empty] | 483.0867
767.2355 | [7 empty] | 547.3972
804.7083 | [7 empty] | 574.1328
785.3989 | [7 empty] | 560.3562
709.7512 | [7 empty] | 506.3841
582.7455 | [7 empty] | 415.7697
413.4692 | [7 empty] | 294.9966
214.3323 | [7 empty] | 152.9191
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
198.7235 | [7 empty] | 141.7826
382.6968 | [7 empty] | 273.0416
540.2896 | [7 empty] | 385.4788
661.6139 | [7 empty] | 472.0397
739.0357 | [7 empty] | 527.2776
767.5525 | [7 empty] | 547.6234
745.0466 | [7 empty] | 531.5662
672.4123 | [7 empty] | 479.744
553.5548 | [7 empty] | 394.9431
395.2549 | [7 empty] | 282.0013
206.8907 | [7 empty] | 147.6097
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
247.9488 | [7 empty] | 176.9033
481.7309 | [7 empty] | 343.6991
683.7672 | [7 empty] | 487.8453
838.6601 | [7 empty] | 598.3564
934.5535 | [7 empty] | 666.7731
964.2077 | [7 empty] | 687.9304
925.6859 | [7 empty] | 660.4464
822.5716 | [7 empty] | 586.8778
663.6825 | [7 empty] | 473.5156
462.2977 | [7 empty] | 329.8342
234.9663 | [7 empty] | 167.6407
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
114.0922 | [7 empty] | 81.401
199.5348 | [7 empty] | 142.3615
252.9077 | [7 empty] | 180.4413
274.4353 | [7 empty] | 195.8006
267.5904 | [7 empty] | 190.917
238.3604 | [7 empty] | 170.0623
194.2918 | [7 empty] | 138.6208
143.4434 | [7 empty] | 102.3421
93.3771 | [7 empty] | 66.6215
50.309 | [7 empty] | 35.8938
18.5096 | [7 empty] | 13.206
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.27181 | [7 empty] | 0.19393
13.4951 | [7 empty] | 9.6283
30.1488 | [7 empty] | 21.5102
46.0926 | [7 empty] | 32.8855
57.8256 | [7 empty] | 41.2566
62.9675 | [7 empty] | 44.9252
60.5293 | [7 empty] | 43.1857
50.9493 | [7 empty] | 36.3506
35.9056 | [7 empty] | 25.6175
17.9473 | [7 empty] | 12.8048
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
4.8762 | [7 empty] | 3.479
15.0688 | [7 empty] | 10.7511
20.9079 | [7 empty] | 14.9171
20.6546 | [7 empty] | 14.7364
13.5622 | [7 empty] | 9.6762
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
16.0134 | [7 empty] | 11.425
25.7784 | [7 empty] | 18.3921
28.5639 | [7 empty] | 20.3794
24.7724 | [7 empty] | 17.6743
15.8698 | [7 empty] | 11.3226
4.1328 | [7 empty] | 2.9486
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
15.9168 | [7 empty] | 11.3561
32.2453 | [7 empty] | 23.0059
46.0387 | [7 empty] | 32.8471
54.6608 | [7 empty] | 38.9987
56.3241 | [7 empty] | 40.1854
50.5145 | [7 empty] | 36.0405
38.2318 | [7 empty] | 27.2771
21.9912 | [7 empty] | 15.69
5.5656 | [7 empty] | 3.9709
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
24.8628 | [7 empty] | 17.7388
65.1232 | [7 empty] | 46.4633
118.4578 | [7 empty] | 84.5157
179.8911 | [7 empty] | 128.3463
242.0918 | [7 empty] | 172.7245
296.0279 | [7 empty] | 211.2062
331.9399 | [7 empty] | 236.8282
340.5315 | [7 empty] | 242.958
314.2444 | [7 empty] | 224.2031
248.4578 | [7 empty] | 177.2664
142.4541 | [7 empty] | 101.6363
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
312.2737 | [7 empty] | 222.797
617.5875 | [7 empty] | 440.6283
891.2579 | [7 empty] | 635.8831
1110.459 | [7 empty] | 792.2759
1256.3121 | [7 empty] | 896.3373
1315.6152 | [7 empty] | 938.6481
1282.0536 | [7 empty] | 914.703
1156.7819 | [7 empty] | 825.3258
948.3255 | [7 empty] | 676.599
671.8281 | [7 empty] | 479.3272
347.7288 | [7 empty] | 248.0931
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
315.9243 | [7 empty] | 225.4016
607.5609 | [7 empty] | 433.4746
856.571 | [7 empty] | 611.1352
1047.4804 | [7 empty] | 747.3427
1168.4612 | [7 empty] | 833.6586
1211.9027 | [7 empty] | 864.6527
1174.7814 | [7 empty] | 838.1678
1058.8302 | [7 empty] | 755.4405
870.5051 | [7 empty] | 621.0767
620.7412 | [7 empty] | 442.8784
324.4874 | [7 empty] | 231.511
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
382.0491 | [7 empty] | 272.5795
741.3727 | [7 empty] | 528.945
1051.032 | [7 empty] | 749.8767
1287.572 | [7 empty] | 918.6402
1433.0788 | [7 empty] | 1022.4545
1476.7924 | [7 empty] | 1053.6427
1416.1134 | [7 empty] | 1010.3503
1256.8869 | [7 empty] | 896.7474
1012.9159 | [7 empty] | 722.6821
704.7375 | [7 empty] | 502.807
357.7703 | [7 empty] | 255.2573
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
171.0246 | [7 empty] | 122.0204
298.7856 | [7 empty] | 213.1737
378.3033 | [7 empty] | 269.9069
410.0683 | [7 empty] | 292.5702
399.417 | [7 empty] | 284.9709
355.4115 | [7 empty] | 253.5744
289.3977 | [7 empty] | 206.4757
213.4347 | [7 empty] | 152.2786
138.7933 | [7 empty] | 99.0245
74.6986 | [7 empty] | 53.295
27.4517 | [7 empty] | 19.5858
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.39718 | [7 empty] | 0.28337
19.9321 | [7 empty] | 14.2209
44.4907 | [7 empty] | 31.7427
67.9535 | [7 empty] | 48.4826
85.1677 | [7 empty] | 60.7644
92.6496 | [7 empty] | 66.1024
88.9742 | [7 empty] | 63.4801
74.818 | [7 empty] | 53.3802
52.6739 | [7 empty] | 37.5811
26.3009 | [7 empty] | 18.7648
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
7.0884 | [7 empty] | 5.0573
21.8941 | [7 empty] | 15.6207
30.3515 | [7 empty] | 21.6548
29.9561 | [7 empty] | 21.3727
19.6501 | [7 empty] | 14.0197
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
22.9155 | [7 empty] | 16.3495
36.8604 | [7 empty] | 26.2987
40.8088 | [7 empty] | 29.1158
35.3612 | [7 empty] | 25.2291
22.6325 | [7 empty] | 16.1475
5.8858 | [7 empty] | 4.1993
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
22.549 | [7 empty] | 16.0879
45.648 | [7 empty] | 32.5683
65.1235 | [7 empty] | 46.4635
77.2579 | [7 empty] | 55.121
79.5448 | [7 empty] | 56.7526
71.2824 | [7 empty] | 50.8577
53.9058 | [7 empty] | 38.46
30.9806 | [7 empty] | 22.1036
7.8315 | [7 empty] | 5.5875
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
34.8891 | [7 empty] | 24.8922
91.3207 | [7 empty] | 65.1543
165.9853 | [7 empty] | 118.425
251.8747 | [7 empty] | 179.7043
338.7064 | [7 empty] | 241.6559
413.8521 | [7 empty] | 295.2698
463.705 | [7 empty] | 330.8383
475.3468 | [7 empty] | 339.1443
438.3214 | [7 empty] | 312.7279
346.2981 | [7 empty] | 247.0723
198.4008 | [7 empty] | 141.5524
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
430.5154 | [7 empty] | 307.1585
850.8387 | [7 empty] | 607.0453
1227.0079 | [7 empty] | 875.4297
1527.7161 | [7 empty] | 1089.9751
1727.1692 | [7 empty] | 1232.2783
1807.4424 | [7 empty] | 1289.5506
1760.1155 | [7 empty] | 1255.7844
1587.0364 | [7 empty] | 1132.2982
1300.1525 | [7 empty] | 927.616
920.444 | [7 empty] | 656.7065
476.0825 | [7 empty] | 339.6692
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
428.5436 | [7 empty] | 305.7517
823.6139 | [7 empty] | 587.6213
1160.43 | [7 empty] | 827.9286
1418.1559 | [7 empty] | 1011.8075
1580.9412 | [7 empty] | 1127.9494
1638.6774 | [7 empty] | 1169.1423
1587.479 | [7 empty] | 1132.614
1429.8925 | [7 empty] | 1020.1812
1174.8311 | [7 empty] | 838.2033
837.2254 | [7 empty] | 597.3328
437.3783 | [7 empty] | 312.055
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
510.6089 | [7 empty] | 364.3026
990.2628 | [7 empty] | 706.5199
1403.0543 | [7 empty] | 1001.033
1717.811 | [7 empty] | 1225.6015
1910.8209 | [7 empty] | 1363.3078
1967.9599 | [7 empty] | 1404.0745
1886.0038 | [7 empty] | 1345.6016
1672.9743 | [7 empty] | 1193.612
1347.4595 | [7 empty] | 961.368
936.9568 | [7 empty] | 668.4878
475.3858 | [7 empty] | 339.1721
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
225.4768 | [7 empty] | 160.8703
393.7035 | [7 empty] | 280.8945
498.2127 | [7 empty] | 355.4583
539.7543 | [7 empty] | 385.0969
525.4511 | [7 empty] | 374.8921
467.3085 | [7 empty] | 333.4092
380.3067 | [7 empty] | 271.3363
280.3308 | [7 empty] | 200.0068
182.1968 | [7 empty] | 129.9914
98.0049 | [7 empty] | 69.9233
35.9957 | [7 empty] | 25.6818
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.51693 | [7 empty] | 0.36881
26.0801 | [7 empty] | 18.6073
58.1875 | [7 empty] | 41.5149
88.8291 | [7 empty] | 63.3767
111.2749 | [7 empty] | 79.3909
120.9882 | [7 empty] | 86.3211
116.1288 | [7 empty] | 82.8541
97.6018 | [7 empty] | 69.6357
68.6783 | [7 empty] | 48.9997
34.2733 | [7 empty] | 24.4528
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
9.1979 | [7 empty] | 6.5624
28.4021 | [7 empty] | 20.2639
39.3552 | [7 empty] | 28.0786
38.8233 | [7 empty] | 27.6992
25.4532 | [7 empty] | 18.16
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
29.4855 | [7 empty] | 21.0369
47.408 | [7 empty] | 33.824
52.4621 | [7 empty] | 37.43
45.4374 | [7 empty] | 32.4181
29.0671 | [7 empty] | 20.7384
7.5536 | [7 empty] | 5.3892
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
28.8542 | [7 empty] | 20.5865
58.3889 | [7 empty] | 41.6585
83.264 | [7 empty] | 59.4061
98.7347 | [7 empty] | 70.444
101.612 | [7 empty] | 72.4968
91.0167 | [7 empty] | 64.9374
68.7982 | [7 empty] | 49.0852
39.5208 | [7 empty] | 28.1968
9.9838 | [7 empty] | 7.1231
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
44.4095 | [7 empty] | 31.6847
116.1939 | [7 empty] | 82.9005
211.1057 | [7 empty] | 150.617
320.2056 | [7 empty] | 228.4562
430.4091 | [7 empty] | 307.0827
525.6745 | [7 empty] | 375.0514
588.7454 | [7 empty] | 420.0505
603.2684 | [7 empty] | 430.4121
556.0417 | [7 empty] | 396.7174
439.1163 | [7 empty] | 313.295
251.4703 | [7 empty] | 179.4158
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
542.5136 | [7 empty] | 387.0656
1071.7506 | [7 empty] | 764.6587
1544.9634 | [7 empty] | 1102.2805
1922.8176 | [7 empty] | 1371.867
2172.9781 | [7 empty] | 1550.3482
2273.0573 | [7 empty] | 1621.7515
2212.6513 | [7 empty] | 1578.6538
1994.275 | [7 empty] | 1422.8495
1633.1242 | [7 empty] | 1165.1803
1155.7112 | [7 empty] | 824.5619
597.5319 | [7 empty] | 426.3194
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
534.9481 | [7 empty] | 381.6678
1027.7225 | [7 empty] | 733.2461
1447.46 | [7 empty] | 1032.715
1768.2646 | [7 empty] | 1261.5985
1970.4936 | [7 empty] | 1405.8822
2041.6872 | [7 empty] | 1456.6765
1977.1542 | [7 empty] | 1410.6344
1780.2179 | [7 empty] | 1270.1268
1462.1191 | [7 empty] | 1043.1738
1041.5679 | [7 empty] | 743.1244
543.9262 | [7 empty] | 388.0734
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
631.7637 | [7 empty] | 450.7426
1224.7918 | [7 empty] | 873.8486
1734.7289 | [7 empty] | 1237.6719
2123.1374 | [7 empty] | 1514.7886
2360.8514 | [7 empty] | 1684.3897
2430.5872 | [7 empty] | 1734.1438
2328.5425 | [7 empty] | 1661.3383
2064.7994 | [7 empty] | 1473.1663
1662.4617 | [7 empty] | 1186.1117
1155.5881 | [7 empty] | 824.474
586.1072 | [7 empty] | 418.1682
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
276.6593 | [7 empty] | 197.3873
482.9118 | [7 empty] | 344.5416
610.8968 | [7 empty] | 435.8547
661.6127 | [7 empty] | 472.0388
643.865 | [7 empty] | 459.3765
572.4284 | [7 empty] | 408.4088
465.7004 | [7 empty] | 332.2619
343.1616 | [7 empty] | 244.8345
222.9581 | [7 empty] | 159.0733
119.8901 | [7 empty] | 85.5376
44.0179 | [7 empty] | 31.4053
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.62933 | [7 empty] | 0.449
31.8502 | [7 empty] | 22.724
71.0406 | [7 empty] | 50.6851
108.4166 | [7 empty] | 77.3517
135.7684 | [7 empty] | 96.8663
147.5723 | [7 empty] | 105.288
141.5994 | [7 empty] | 101.0265
118.9703 | [7 empty] | 84.8814
83.6869 | [7 empty] | 59.7079
41.7487 | [7 empty] | 29.7863
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
11.1742 | [7 empty] | 7.9724
34.4982 | [7 empty] | 24.6133
47.7882 | [7 empty] | 34.0953
47.1277 | [7 empty] | 33.624
30.8873 | [7 empty] | 22.0371
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
35.6279 | [7 empty] | 25.4194
57.2681 | [7 empty] | 40.8589
63.3546 | [7 empty] | 45.2014
54.8547 | [7 empty] | 39.137
35.0803 | [7 empty] | 25.0286
9.112 | [7 empty] | 6.5011
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
34.7412 | [7 empty] | 24.7867
70.2831 | [7 empty] | 50.1447
100.1971 | [7 empty] | 71.4873
118.7798 | [7 empty] | 84.7455
122.2057 | [7 empty] | 87.1898
109.4311 | [7 empty] | 78.0755
82.693 | [7 empty] | 58.9987
47.4881 | [7 empty] | 33.8812
11.9916 | [7 empty] | 8.5556
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
53.286 | [7 empty] | 38.0178
139.3822 | [7 empty] | 99.4446
253.1647 | [7 empty] | 180.6247
383.8929 | [7 empty] | 273.8949
515.87 | [7 empty] | 368.0562
629.8734 | [7 empty] | 449.3939
705.2476 | [7 empty] | 503.1709
722.4413 | [7 empty] | 515.4381
665.6981 | [7 empty] | 474.9537
525.5663 | [7 empty] | 374.9743
300.8931 | [7 empty] | 214.6773
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
646.6442 | [7 empty] | 461.3593
1277.1196 | [7 empty] | 911.1827
1840.5131 | [7 empty] | 1313.1454
2290.0335 | [7 empty] | 1633.8634
2587.2733 | [7 empty] | 1845.9342
2705.7071 | [7 empty] | 1930.4329
2633.0981 | [7 empty] | 1878.6287
2372.5916 | [7 empty] | 1692.7659
1942.4115 | [7 empty] | 1385.8466
1374.2179 | [7 empty] | 980.4592
710.3158 | [7 empty] | 506.7869
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
633.5945 | [7 empty] | 452.0488
1216.9267 | [7 empty] | 868.2371
1713.4983 | [7 empty] | 1222.5246
2092.7291 | [7 empty] | 1493.0933
2331.469 | [7 empty] | 1663.4263
2415.0874 | [7 empty] | 1723.0853
2338.1558 | [7 empty] | 1668.1971
2104.7257 | [7 empty] | 1501.6524
1728.2028 | [7 empty] | 1233.0158
1230.8051 | [7 empty] | 878.1389
642.5859 | [7 empty] | 458.4639
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
743.7565 | [7 empty] | 530.6458
1441.5583 | [7 empty] | 1028.5043
2041.2456 | [7 empty] | 1456.3615
2497.6731 | [7 empty] | 1782.0074
2776.6436 | [7 empty] | 1981.0437
2857.9648 | [7 empty] | 2039.0637
2737.3115 | [7 empty] | 1952.9816
2426.6798 | [7 empty] | 1731.3561
1953.3541 | [7 empty] | 1393.6538
1357.4605 | [7 empty] | 968.5034
688.3287 | [7 empty] | 491.0998
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
323.8295 | [7 empty] | 231.0417
565.1167 | [7 empty] | 403.1922
714.7215 | [7 empty] | 509.9303
773.8761 | [7 empty] | 552.1351
752.9413 | [7 empty] | 537.1988
669.2468 | [7 empty] | 477.4855
544.3405 | [7 empty] | 388.369
401.0158 | [7 empty] | 286.1116
260.4861 | [7 empty] | 185.8483
140.0367 | [7 empty] | 99.9115
51.4018 | [7 empty] | 36.6735
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.73274 | [7 empty] | 0.52279
37.1584 | [7 empty] | 26.5113
82.8635 | [7 empty] | 59.1204
126.4319 | [7 empty] | 90.205
158.293 | [7 empty] | 112.9369
172.0163 | [7 empty] | 122.728
165.0166 | [7 empty] | 117.7339
138.6135 | [7 empty] | 98.8962
97.482 | [7 empty] | 69.5502
48.6188 | [7 empty] | 34.6879
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
12.9885 | [7 empty] | 9.2669
40.0942 | [7 empty] | 28.6059
55.5282 | [7 empty] | 39.6176
54.7487 | [7 empty] | 39.0614
35.8736 | [7 empty] | 25.5946
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
41.2538 | [7 empty] | 29.4333
66.2979 | [7 empty] | 47.3013
73.3285 | [7 empty] | 52.3175
63.4767 | [7 empty] | 45.2885
40.5849 | [7 empty] | 28.956
10.5384 | [7 empty] | 7.5188
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
40.1244 | [7 empty] | 28.6274
81.1582 | [7 empty] | 57.9037
115.6772 | [7 empty] | 82.5319
137.1024 | [7 empty] | 97.818
141.0273 | [7 empty] | 100.6184
126.2587 | [7 empty] | 90.0814
95.3886 | [7 empty] | 68.0566
54.7667 | [7 empty] | 39.0743
13.8256 | [7 empty] | 9.8641
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
61.3899 | [7 empty] | 43.7997
160.5492 | [7 empty] | 114.5466
291.5523 | [7 empty] | 208.013
442.0129 | [7 empty] | 315.3616
593.8495 | [7 empty] | 423.692
724.9377 | [7 empty] | 517.2192
811.5221 | [7 empty] | 578.9943
831.1371 | [7 empty] | 592.9889
765.7003 | [7 empty] | 546.302
604.3945 | [7 empty] | 431.2155
345.9522 | [7 empty] | 246.8255
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
741.397 | [7 empty] | 528.9623
1463.9672 | [7 empty] | 1044.4924
2109.3708 | [7 empty] | 1504.9666
2624.0382 | [7 empty] | 1872.1648
2964.0466 | [7 empty] | 2114.7496
3099.1175 | [7 empty] | 2211.1182
3015.3585 | [7 empty] | 2151.3589
2716.4997 | [7 empty] | 1938.1331
2223.529 | [7 empty] | 1586.4147
1572.795 | [7 empty] | 1122.1374
812.7983 | [7 empty] | 579.9048
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
723.0524 | [7 empty] | 515.8741
1388.4825 | [7 empty] | 990.6365
1954.6866 | [7 empty] | 1394.6045
2386.8439 | [7 empty] | 1702.9345
2658.6322 | [7 empty] | 1896.8465
2753.4629 | [7 empty] | 1964.5051
2665.2483 | [7 empty] | 1901.5669
2398.7097 | [7 empty] | 1711.4004
1969.2234 | [7 empty] | 1404.976
1402.1926 | [7 empty] | 1000.4182
731.9267 | [7 empty] | 522.2056
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
844.9631 | [7 empty] | 602.8533
1637.4186 | [7 empty] | 1168.2442
2318.1592 | [7 empty] | 1653.9302
2835.9863 | [7 empty] | 2023.3827
3152.1676 | [7 empty] | 2248.9677
3243.8948 | [7 empty] | 2314.4121
3106.3826 | [7 empty] | 2216.3017
2753.3673 | [7 empty] | 1964.4368
2215.918 | [7 empty] | 1580.9845
1539.6465 | [7 empty] | 1098.487
780.5678 | [7 empty] | 556.9094
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
366.3036 | [7 empty] | 261.3456
639.1262 | [7 empty] | 455.9955
808.1811 | [7 empty] | 576.6106
874.9165 | [7 empty] | 624.2241
851.0983 | [7 empty] | 607.2306
756.3595 | [7 empty] | 539.6376
615.0863 | [7 empty] | 438.8438
453.0544 | [7 empty] | 323.2394
294.2366 | [7 empty] | 209.9281
158.1525 | [7 empty] | 112.8366
58.0405 | [7 empty] | 41.41
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.82568 | [7 empty] | 0.58909
41.9279 | [7 empty] | 29.9142
93.4849 | [7 empty] | 66.6984
142.6138 | [7 empty] | 101.7502
178.5222 | [7 empty] | 127.3697
193.9659 | [7 empty] | 138.3883
186.0408 | [7 empty] | 132.734
156.2466 | [7 empty] | 111.4768
109.8635 | [7 empty] | 78.384
54.784 | [7 empty] | 39.0866
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
14.6146 | [7 empty] | 10.4271
45.1089 | [7 empty] | 32.1837
62.4632 | [7 empty] | 44.5654
61.5758 | [7 empty] | 43.9323
40.3398 | [7 empty] | 28.7811
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
46.2816 | [7 empty] | 33.0204
74.3663 | [7 empty] | 53.0579
82.2391 | [7 empty] | 58.6749
71.1782 | [7 empty] | 50.7833
45.5011 | [7 empty] | 32.4635
11.8121 | [7 empty] | 8.4275
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
44.9259 | [7 empty] | 32.0531
90.8564 | [7 empty] | 64.8231
129.4798 | [7 empty] | 92.3796
153.4368 | [7 empty] | 109.4721
157.8038 | [7 empty] | 112.5878
141.2553 | [7 empty] | 100.781
106.7011 | [7 empty] | 76.1277
61.2513 | [7 empty] | 43.7008
15.4592 | [7 empty] | 11.0296
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
68.6037 | [7 empty] | 48.9465
179.388 | [7 empty] | 127.9874
325.7118 | [7 empty] | 232.3846
493.7227 | [7 empty] | 352.2549
663.2168 | [7 empty] | 473.1834
809.4887 | [7 empty] | 577.5435
906.0275 | [7 empty] | 646.4208
927.7794 | [7 empty] | 661.94
854.5981 | [7 empty] | 609.7276
674.4575 | [7 empty] | 481.2032
385.9943 | [7 empty] | 275.3942
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
825.3977 | [7 empty] | 588.894
1629.5837 | [7 empty] | 1162.6543
2347.6374 | [7 empty] | 1674.9619
2919.9878 | [7 empty] | 2083.315
3297.8338 | [7 empty] | 2352.8958
3447.5828 | [7 empty] | 2459.7367
3353.8885 | [7 empty] | 2392.889
3021.0118 | [7 empty] | 2155.3924
2472.3998 | [7 empty] | 1763.9758
1748.5626 | [7 empty] | 1247.5418
903.4934 | [7 empty] | 644.6128
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
802.0244 | [7 empty] | 572.218
1539.9018 | [7 empty] | 1098.6692
2167.5271 | [7 empty] | 1546.4592
2646.3435 | [7 empty] | 1888.0789
2947.2387 | [7 empty] | 2102.7577
3051.9063 | [7 empty] | 2177.4346
2953.6881 | [7 empty] | 2107.3591
2657.9065 | [7 empty] | 1896.3287
2181.6852 | [7 empty] | 1556.5605
1553.2449 | [7 empty] | 1108.189
810.6528 | [7 empty] | 578.3741
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
933.9156 | [7 empty] | 666.318
1809.5324 | [7 empty] | 1291.0417
2561.4538 | [7 empty] | 1827.5129
3133.1705 | [7 empty] | 2235.4139
3481.9772 | [7 empty] | 2484.276
3582.7803 | [7 empty] | 2556.1957
3430.4034 | [7 empty] | 2447.4798
3040.124 | [7 empty] | 2169.0283
2446.3456 | [7 empty] | 1745.3869
1699.5037 | [7 empty] | 1212.5399
861.4868 | [7 empty] | 614.6424
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
403.4655 | [7 empty] | 287.8593
703.8669 | [7 empty] | 502.1858
889.9201 | [7 empty] | 634.9287
963.2685 | [7 empty] | 687.2604
936.9122 | [7 empty] | 668.456
832.5033 | [7 empty] | 593.9636
676.912 | [7 empty] | 482.9544
498.5227 | [7 empty] | 355.6795
323.72 | [7 empty] | 230.9635
173.9749 | [7 empty] | 124.1253
63.8375 | [7 empty] | 45.546
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.90678 | [7 empty] | 0.64696
46.0895 | [7 empty] | 32.8833
102.7507 | [7 empty] | 73.3092
156.7275 | [7 empty] | 111.8199
196.1625 | [7 empty] | 139.9555
213.1025 | [7 empty] | 152.0416
204.3671 | [7 empty] | 145.8092
171.6139 | [7 empty] | 122.4409
120.6518 | [7 empty] | 86.0811
60.1548 | [7 empty] | 42.9185
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
16.029 | [7 empty] | 11.4361
49.4695 | [7 empty] | 35.2949
68.4924 | [7 empty] | 48.8671
67.5101 | [7 empty] | 48.1662
44.221 | [7 empty] | 31.5503
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
50.6383 | [7 empty] | 36.1288
81.3563 | [7 empty] | 58.0451
89.9572 | [7 empty] | 64.1815
77.8476 | [7 empty] | 55.5417
49.7575 | [7 empty] | 35.5003
12.9146 | [7 empty] | 9.2142
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
49.076 | [7 empty] | 35.0141
99.2371 | [7 empty] | 70.8024
141.4048 | [7 empty] | 100.8877
167.5461 | [7 empty] | 119.5387
172.2919 | [7 empty] | 122.9246
154.2035 | [7 empty] | 110.0191
116.4662 | [7 empty] | 83.0948
66.8477 | [7 empty] | 47.6936
16.8687 | [7 empty] | 12.0353
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
74.8226 | [7 empty] | 53.3835
195.6253 | [7 empty] | 139.5722
355.1478 | [7 empty] | 253.3862
538.2725 | [7 empty] | 384.0397
722.966 | [7 empty] | 515.8124
882.3002 | [7 empty] | 629.4921
987.3934 | [7 empty] | 704.4727
1010.9667 | [7 empty] | 721.2914
931.1022 | [7 empty] | 664.3107
734.7393 | [7 empty] | 524.2123
420.4387 | [7 empty] | 299.9691
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
897.4282 | [7 empty] | 640.2854
1771.5672 | [7 empty] | 1263.9548
2551.8573 | [7 empty] | 1820.6661
3173.5902 | [7 empty] | 2264.252
3583.7942 | [7 empty] | 2556.9191
3746.0496 | [7 empty] | 2672.6829
3643.7788 | [7 empty] | 2599.7161
3281.7117 | [7 empty] | 2341.3932
2685.4146 | [7 empty] | 1915.9549
1898.9718 | [7 empty] | 1354.8538
981.0857 | [7 empty] | 699.9723
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
869.365 | [7 empty] | 620.2633
1668.9889 | [7 empty] | 1190.7686
2348.9331 | [7 empty] | 1675.8863
2867.4644 | [7 empty] | 2045.8414
3193.1028 | [7 empty] | 2278.1736
3306.0893 | [7 empty] | 2358.7858
3199.2919 | [7 empty] | 2282.5894
2878.557 | [7 empty] | 2053.7556
2362.5073 | [7 empty] | 1685.5711
1681.7713 | [7 empty] | 1199.8884
877.6225 | [7 empty] | 626.1547
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
1009.3242 | [7 empty] | 720.1195
1955.4034 | [7 empty] | 1395.1159
2767.6008 | [7 empty] | 1974.592
3384.916 | [7 empty] | 2415.026
3761.2894 | [7 empty] | 2683.5561
3869.7063 | [7 empty] | 2760.908
3704.6748 | [7 empty] | 2643.1634
3282.7914 | [7 empty] | 2342.1635
2641.295 | [7 empty] | 1884.477
1834.714 | [7 empty] | 1309.008
929.9122 | [7 empty] | 663.4617
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
434.7762 | [7 empty] | 310.1985
758.3999 | [7 empty] | 541.0933
958.7532 | [7 empty] | 684.0388
1037.6508 | [7 empty] | 740.3297
1009.1387 | [7 empty] | 719.9872
896.5737 | [7 empty] | 639.6758
728.9208 | [7 empty] | 520.061
536.7612 | [7 empty] | 382.9615
348.5087 | [7 empty] | 248.6495
187.2743 | [7 empty] | 133.6141
68.7089 | [7 empty] | 49.0215
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.97488 | [7 empty] | 0.69555
49.5828 | [7 empty] | 35.3757
110.5264 | [7 empty] | 78.8569
168.5685 | [7 empty] | 120.2681
210.9581 | [7 empty] | 150.5116
229.1488 | [7 empty] | 163.4901
219.7297 | [7 empty] | 156.7699
184.4925 | [7 empty] | 131.6294
129.6905 | [7 empty] | 92.5299
64.6534 | [7 empty] | 46.128
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
17.211 | [7 empty] | 12.2795
53.1128 | [7 empty] | 37.8943
73.5284 | [7 empty] | 52.4601
72.4654 | [7 empty] | 51.7017
47.4612 | [7 empty] | 33.862
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
54.2608 | [7 empty] | 38.7133
87.1667 | [7 empty] | 62.1906
96.3707 | [7 empty] | 68.7574
83.3882 | [7 empty] | 59.4947
53.2925 | [7 empty] | 38.0224
13.83 | [7 empty] | 9.8673
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
52.5145 | [7 empty] | 37.4674
106.1788 | [7 empty] | 75.7551
151.2792 | [7 empty] | 107.9327
179.2258 | [7 empty] | 127.8717
184.2814 | [7 empty] | 131.4787
164.9155 | [7 empty] | 117.6618
124.5424 | [7 empty] | 88.8569
71.4748 | [7 empty] | 50.9949
18.0338 | [7 empty] | 12.8665
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
79.9566 | [7 empty] | 57.0464
209.0258 | [7 empty] | 149.133
379.4334 | [7 empty] | 270.7132
575.016 | [7 empty] | 410.255
772.2304 | [7 empty] | 550.961
942.3162 | [7 empty] | 672.3115
1054.4398 | [7 empty] | 752.308
1079.4925 | [7 empty] | 770.1823
994.103 | [7 empty] | 709.2598
784.3657 | [7 empty] | 559.6191
448.7857 | [7 empty] | 320.1938
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
956.4438 | [7 empty] | 682.3912
1887.8586 | [7 empty] | 1346.9249
2719.069 | [7 empty] | 1939.9661
3381.1676 | [7 empty] | 2412.3517
3817.7805 | [7 empty] | 2723.8606
3990.1892 | [7 empty] | 2846.8685
3880.8251 | [7 empty] | 2768.8409
3494.8185 | [7 empty] | 2493.4378
2859.4843 | [7 empty] | 2040.1478
2021.8413 | [7 empty] | 1442.5171
1044.4498 | [7 empty] | 745.1805
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
924.0978 | [7 empty] | 659.3134
1773.8714 | [7 empty] | 1265.5988
2496.2737 | [7 empty] | 1781.009
3047 | [7 empty] | 2173.9341
3392.6589 | [7 empty] | 2420.5503
3512.3258 | [7 empty] | 2505.9287
3398.498 | [7 empty] | 2424.7164
3057.4612 | [7 empty] | 2181.3978
2509.067 | [7 empty] | 1790.1367
1785.9078 | [7 empty] | 1274.1864
931.8646 | [7 empty] | 664.8547
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
1070.0951 | [7 empty] | 763.4776
2072.9163 | [7 empty] | 1478.9575
2933.6107 | [7 empty] | 2093.0346
3587.5716 | [7 empty] | 2559.6141
3986.0535 | [7 empty] | 2843.9178
4100.5119 | [7 empty] | 2925.5801
3925.219 | [7 empty] | 2800.5144
3477.85 | [7 empty] | 2481.3314
2797.9391 | [7 empty] | 1996.2373
1943.3164 | [7 empty] | 1386.4922
984.8516 | [7 empty] | 702.6592
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
459.7818 | [7 empty] | 328.0391
801.9342 | [7 empty] | 572.1536
1013.682 | [7 empty] | 723.2287
1096.9847 | [7 empty] | 782.6625
1066.7303 | [7 empty] | 761.0769
947.6417 | [7 empty] | 676.1111
770.3586 | [7 empty] | 549.6255
567.2155 | [7 empty] | 404.6896
368.2434 | [7 empty] | 262.7295
197.858 | [7 empty] | 141.1651
72.584 | [7 empty] | 51.7863
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
1.029 | [7 empty] | 0.73415
52.3571 | [7 empty] | 37.3551
116.6994 | [7 empty] | 83.2612
177.9649 | [7 empty] | 126.9721
222.6943 | [7 empty] | 158.8851
241.872 | [7 empty] | 172.5677
231.9058 | [7 empty] | 165.4571
194.6957 | [7 empty] | 138.909
136.8486 | [7 empty] | 97.6369
68.2144 | [7 empty] | 48.6687
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
18.1435 | [7 empty] | 12.9448
55.986 | [7 empty] | 39.9442
77.4983 | [7 empty] | 55.2925
76.37 | [7 empty] | 54.4875
50.0131 | [7 empty] | 35.6827
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
57.0965 | [7 empty] | 40.7365
91.713 | [7 empty] | 65.4342
101.3869 | [7 empty] | 72.3362
87.7195 | [7 empty] | 62.585
56.0547 | [7 empty] | 39.9932
14.545 | [7 empty] | 10.3774
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
55.1916 | [7 empty] | 39.3774
111.5808 | [7 empty] | 79.6092
158.9598 | [7 empty] | 113.4126
188.3063 | [7 empty] | 134.3504
193.5986 | [7 empty] | 138.1262
173.236 | [7 empty] | 123.5982
130.8126 | [7 empty] | 93.3305
75.0654 | [7 empty] | 53.5567
18.9375 | [7 empty] | 13.5113
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
83.9312 | [7 empty] | 59.8821
219.3949 | [7 empty] | 156.531
398.2164 | [7 empty] | 284.1142
603.4205 | [7 empty] | 430.5207
810.2957 | [7 empty] | 578.1193
988.6663 | [7 empty] | 705.3809
1106.1941 | [7 empty] | 789.2331
1132.363 | [7 empty] | 807.9037
1042.687 | [7 empty] | 743.9228
822.6169 | [7 empty] | 586.91
470.6244 | [7 empty] | 335.775
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
1001.5887 | [7 empty] | 714.6006
1976.7714 | [7 empty] | 1410.3613
2846.8474 | [7 empty] | 2031.1318
3539.7096 | [7 empty] | 2525.4662
3996.3994 | [7 empty] | 2851.2993
4176.461 | [7 empty] | 2979.7673
4061.5897 | [7 empty] | 2897.8104
3657.2416 | [7 empty] | 2609.3214
2992.0842 | [7 empty] | 2134.7535
2115.3889 | [7 empty] | 1509.2603
1092.6669 | [7 empty] | 779.5818
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
965.429 | [7 empty] | 688.8018
1853.0285 | [7 empty] | 1322.0747
2607.412 | [7 empty] | 1860.3026
3182.3464 | [7 empty] | 2270.4993
3543.0129 | [7 empty] | 2527.823
3667.6247 | [7 empty] | 2616.7294
3548.4174 | [7 empty] | 2531.6789
3192.0245 | [7 empty] | 2277.4043
2619.2391 | [7 empty] | 1868.7408
1864.1443 | [7 empty] | 1330.0056
972.5924 | [7 empty] | 693.9126
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
1115.347 | [7 empty] | 795.7634
2160.3667 | [7 empty] | 1541.3505
3057.0759 | [7 empty] | 2181.1229
3738.1985 | [7 empty] | 2667.0814
4153.0097 | [7 empty] | 2963.0356
4271.8498 | [7 empty] | 3047.824
4088.8377 | [7 empty] | 2917.2509
3622.471 | [7 empty] | 2584.5137
2914.006 | [7 empty] | 2079.0473
2023.7358 | [7 empty] | 1443.8688
1025.5083 | [7 empty] | 731.6664
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
478.1194 | [7 empty] | 341.1225
833.8386 | [7 empty] | 594.9164
1053.91 | [7 empty] | 751.9301
1140.4097 | [7 empty] | 813.6447
1108.8516 | [7 empty] | 791.1291
984.9666 | [7 empty] | 702.7412
800.6244 | [7 empty] | 571.2191
589.4439 | [7 empty] | 420.5488
382.6377 | [7 empty] | 272.9994
205.5723 | [7 empty] | 146.6691
75.4065 | [7 empty] | 53.8001
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
1.0683 | [7 empty] | 0.76221
54.3724 | [7 empty] | 38.7929
121.18 | [7 empty] | 86.458
184.7805 | [7 empty] | 131.8348
231.2011 | [7 empty] | 164.9544
251.0876 | [7 empty] | 179.1427
240.7188 | [7 empty] | 171.7449
202.0754 | [7 empty] | 144.1741
142.0221 | [7 empty] | 101.3281
70.7863 | [7 empty] | 50.5037
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
18.8131 | [7 empty] | 13.4225
58.0474 | [7 empty] | 41.4149
80.3443 | [7 empty] | 57.323
79.1671 | [7 empty] | 56.4831
51.8399 | [7 empty] | 36.9861
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
59.1043 | [7 empty] | 42.169
94.9294 | [7 empty] | 67.729
104.9328 | [7 empty] | 74.8661
90.7789 | [7 empty] | 64.7677
58.0042 | [7 empty] | 41.3841
15.0492 | [7 empty] | 10.7371
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
57.0683 | [7 empty] | 40.7164
115.3647 | [7 empty] | 82.3089
164.3353 | [7 empty] | 117.2478
194.6561 | [7 empty] | 138.8807
200.1082 | [7 empty] | 142.7706
179.0442 | [7 empty] | 127.7422
135.1858 | [7 empty] | 96.4506
77.5676 | [7 empty] | 55.3419
19.5667 | [7 empty] | 13.9602
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
86.6886 | [7 empty] | 61.8495
226.5824 | [7 empty] | 161.6591
411.2243 | [7 empty] | 293.395
623.074 | [7 empty] | 444.5428
836.6098 | [7 empty] | 596.8935
1020.6785 | [7 empty] | 728.2205
1141.906 | [7 empty] | 814.7123
1168.8116 | [7 empty] | 833.9086
1076.1495 | [7 empty] | 767.7972
848.9382 | [7 empty] | 605.6894
485.6379 | [7 empty] | 346.4867
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
1032.2082 | [7 empty] | 736.4465
2037.0161 | [7 empty] | 1453.3439
2933.3393 | [7 empty] | 2092.841
3646.9169 | [7 empty] | 2601.955
4117.0604 | [7 empty] | 2937.387
4302.1636 | [7 empty] | 3069.452
4183.451 | [7 empty] | 2984.7545
3766.6255 | [7 empty] | 2687.3632
3081.2914 | [7 empty] | 2198.3999
2178.2582 | [7 empty] | 1554.1155
1125.0377 | [7 empty] | 802.6773
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
992.7591 | [7 empty] | 708.3009
1905.312 | [7 empty] | 1359.3773
2680.7364 | [7 empty] | 1912.6171
3271.5408 | [7 empty] | 2334.1366
3641.9844 | [7 empty] | 2598.4358
3769.7339 | [7 empty] | 2689.5809
3646.8757 | [7 empty] | 2601.9257
3280.2955 | [7 empty] | 2340.3828
2691.4256 | [7 empty] | 1920.2435
1915.3461 | [7 empty] | 1366.5363
999.2153 | [7 empty] | 712.9072
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
1144.4238 | [7 empty] | 816.5086
2216.4864 | [7 empty] | 1581.39
3136.2058 | [7 empty] | 2237.5795
3834.612 | [7 empty] | 2735.8693
4259.7368 | [7 empty] | 3039.1818
4381.235 | [7 empty] | 3125.8668
4193.1579 | [7 empty] | 2991.68
3714.5572 | [7 empty] | 2650.2141
2987.8126 | [7 empty] | 2131.7058
2074.8061 | [7 empty] | 1480.3058
1051.2927 | [7 empty] | 750.0627
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
489.5233 | [7 empty] | 349.2587
853.6504 | [7 empty] | 609.0514
1078.8538 | [7 empty] | 769.7266
1167.2959 | [7 empty] | 832.8271
1134.892 | [7 empty] | 809.708
1008.0072 | [7 empty] | 719.1799
819.2792 | [7 empty] | 584.5287
603.124 | [7 empty] | 430.3091
391.483 | [7 empty] | 279.3102
210.3055 | [7 empty] | 150.046
77.1357 | [7 empty] | 55.0338
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
1.0923 | [7 empty] | 0.77932
55.5992 | [7 empty] | 39.6682
123.9034 | [7 empty] | 88.401
188.9165 | [7 empty] | 134.7857
236.3551 | [7 empty] | 168.6316
256.6619 | [7 empty] | 183.1198
246.0409 | [7 empty] | 175.5421
206.5246 | [7 empty] | 147.3485
145.136 | [7 empty] | 103.5498
72.3318 | [7 empty] | 51.6064
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
19.21 | [7 empty] | 13.7057
59.2672 | [7 empty] | 42.2852
82.0253 | [7 empty] | 58.5224
80.8163 | [7 empty] | 57.6598
52.915 | [7 empty] | 37.7531
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
60.2551 | [7 empty] | 42.99
96.7693 | [7 empty] | 69.0417
106.957 | [7 empty] | 76.3103
92.5219 | [7 empty] | 66.0113
59.1125 | [7 empty] | 42.1748
15.3353 | [7 empty] | 10.9412
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
58.1176 | [7 empty] | 41.465
117.4756 | [7 empty] | 83.815
167.3276 | [7 empty] | 119.3827
198.183 | [7 empty] | 141.397
203.7158 | [7 empty] | 145.3445
182.256 | [7 empty] | 130.0337
137.5986 | [7 empty] | 98.1721
78.945 | [7 empty] | 56.3247
19.9122 | [7 empty] | 14.2067
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
88.1891 | [7 empty] | 62.92
230.4841 | [7 empty] | 164.4428
418.2686 | [7 empty] | 298.4209
633.6915 | [7 empty] | 452.118
850.791 | [7 empty] | 607.0113
1037.8883 | [7 empty] | 740.4991
1161.0575 | [7 empty] | 828.3763
1188.3095 | [7 empty] | 847.8197
1094.0052 | [7 empty] | 780.5366
862.9478 | [7 empty] | 615.6848
493.6086 | [7 empty] | 352.1735
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
1047.8581 | [7 empty] | 747.6123
2067.719 | [7 empty] | 1475.2494
2977.2905 | [7 empty] | 2124.1987
3701.2347 | [7 empty] | 2640.709
4178.0137 | [7 empty] | 2980.8751
4365.474 | [7 empty] | 3114.6218
4244.6417 | [7 empty] | 3028.412
3821.3839 | [7 empty] | 2726.4315
3125.8122 | [7 empty] | 2230.164
2209.5374 | [7 empty] | 1576.4321
1141.0927 | [7 empty] | 814.132
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
1005.6918 | [7 empty] | 717.528
1929.9638 | [7 empty] | 1376.9656
2715.1834 | [7 empty] | 1937.1939
3313.2896 | [7 empty] | 2363.923
3688.1379 | [7 empty] | 2631.3648
3817.1724 | [7 empty] | 2723.4267
3692.4452 | [7 empty] | 2634.438
3320.994 | [7 empty] | 2369.4198
2724.5797 | [7 empty] | 1943.8979
1938.7706 | [7 empty] | 1383.249
1011.3471 | [7 empty] | 721.5628
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
1156.9035 | [7 empty] | 825.4126
2240.4616 | [7 empty] | 1598.4955
3169.8529 | [7 empty] | 2261.5856
3875.4141 | [7 empty] | 2764.9802
4304.687 | [7 empty] | 3071.2523
4427.0813 | [7 empty] | 3158.5766
4236.6667 | [7 empty] | 3022.7221
3752.7728 | [7 empty] | 2677.4798
3018.2884 | [7 empty] | 2153.4493
2095.7865 | [7 empty] | 1495.2746
1061.8308 | [7 empty] | 757.5813
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
493.8279 | [7 empty] | 352.33
861.0822 | [7 empty] | 614.3538
1088.1516 | [7 empty] | 776.3603
1177.2535 | [7 empty] | 839.9316
1144.4736 | [7 empty] | 816.5442
1016.4292 | [7 empty] | 725.1887
826.0525 | [7 empty] | 589.3613
608.0574 | [7 empty] | 433.8289
394.6508 | [7 empty] | 281.5704
211.9888 | [7 empty] | 151.247
77.7463 | [7 empty] | 55.4694
0.01 | [7 empty] | 0.0071347
0.01 | [7 empty] | 0.0071347
1.1006 | [7 empty] | 0.78523
56.0198 | [7 empty] | 39.9683
124.8301 | [7 empty] | 89.0621
190.3129 | [7 empty] | 135.782
238.0814 | [7 empty] | 169.8632

## Test2
Test 2 |  | Sizing of 12 x 10 bore field based on an unbalanced load for a ten year period with two peak durations (6 hours and durations used by Shonder et al. (2000)) | [21 empty] | Variuos peak load durations used by Shonder et al. (2000) | [5 empty] | Peak load duration of 6 hours
[24 empty] | Rb calculated by tool |  |  | Imposed Rb |  |  | Rb calculated by tool |  |  | Imposed Rb
| Month | Number of days | Ground monthly cooling averaged load | Ground monthly heating averaged load | Building monthly cooling peak Load | Peak cooling hours | Building monthly heating peak load | Peak heating hours | Hourly Ground Load | Month | Ground monthly averaged load | Ground monthly cooling peak Load | Peak cooling hours | Ground monthly heating peak load | Peak heating hours |  | Ground yearly, monthly and hourly pulses | Parameter | Value | Units |  | Level | Sizing tool | Borehole length | Difference from mean | Rb calculated by tool | Borehole length | Difference from mean | Imposed Rb=0.113 m.k.W-1 | Borehole length | Difference from mean | Rb calculated by tool | Borehole length | Difference from mean | Imposed Rb=0.113 m.k.W-1
|  | (day) | (MJ) | (MJ) | (kW) | (hr) | (kW) | (hr) | (W) |  | (W) | (W) | (hr) | (W) | (hr) |  | (W) | Nb | 12×10 | ---- |  |  |  | (m) | % | (m.K/W) | m | % | (m.K/W) | (m) | % | (m.K/W) | m | % | (m.K/W)
|  |  | qm,C | qm,H | qh,C | th,C | qh,H | th,H | qh |  | qm | qh,C | th,C | qh,H | th,H |  | Cooling | B | 6 | m | A | L2 | Classic ASHRAE sizing equation | 91.3 | 1.3699 | 0.103 | 94.6 | 0.12049 | 0.113 | 86.1 | 2.0056 | 0.103 | 89.7 | 0.71377 | 0.113
Loads reported by shonder et al. (2000) | 1 | 31 | 11 | 267858 | 45 | 2 | 523 | 11 | 100002.6135 | 1 | 100002.6135 | -57352.4568 | 2 | 395127.1394 | 11 | qh |  | D | 3 | m | B | L2 | Modified ASHRAE sizing equation | ----- | ----- | ----- | ---- | ----- | ---- | 85 | 0.70238 | 0.101 | 89.1 | 0.040099 | 0.113
| 2 | 28 | 43 | 187830 | 17 | 1 | 497 | 5 | 100002.6135 | 2 | 77623.5946 | -21666.4837 | 1 | 375484.1076 | 5 | qm |  | rb | 54 | mm | C | L2 | Modified + ASHRAE sizing equation -B | 91.6 | 1.703 | 0.104 | 94.9 | 0.438 | 0.113 | 86.6 | 2.598 | 0.104 | 90.2 | 1.2752 | 0.113
| 3 | 31 | 4726 | 105953 | 88 | 1 | 496 | 2 | 100002.6135 | 3 | 37793.8321 | -112155.9155 | 1 | 374728.6064 | 2 | qy |  | rp,o,rp,i | 16.7, 13.7 | mm | D | L2 | Modified + ASHRAE sizing equation- F | 91.6 | 1.703 | 0.104 | 94.8 | 0.33216 | 0.113 | 86.6 | 2.598 | 0.104 | 90.2 | 1.2752 | 0.113
| 4 | 30 | 18480 | 43635 | 116 | 2 | 265 | 3 | 100002.6135 | 4 | 9704.8611 | -147841.8886 | 2 | 200207.824 | 3 |  | Heating | 2dp | 47.1 | mm | E | L2 | Alternative method | 88.8 | -1.4058 | 0.103 | 92.2 | -2.4196 | 0.113 | 83.1 | -1.5486 | 0.103 | 86.9 | -2.43 | 0.113
| 5 | 31 | 100622 | 6447 | 276 | 2 | 144 | 1 | 100002.6135 | 5 | -35160.917 | -351761.7348 | 2 | 108792.176 | 1 | qh | 395127.1394 | mf | 29 | kg.s-1 | Est | L2 | Alternative method (short-term effects) | 88 | -2.294 | 0.103 | 91.4 | -3.2662 | 0.113 | 81.9 | -2.9703 | 0.102 | 85.5 | -4.0019 | 0.113
| 6 | 30 | 210198 | 101 | 442 | 3 | 67 | 1 | 100002.6135 | 6 | -81055.9414 | -563328.5753 | 3 | 50618.5819 | 1 | qm | 100002.6135 | ρf | 1026 | kg.m-3 | F | L2 | GHX design tool box | 85 | -5.6249 | 0.101 | 108 | 14.3025 | 0.113 | 79 | -6.406 | 0.101 | 102 | 14.524 | 0.113
| 7 | 31 | 281505 | 3 | 420 | 5 | 62 | 1 | 100002.6135 | 7 | -105100.8065 | -535289.5965 | 5 | 46841.0758 | 1 | qy | 1763 | cp,f | 4019 | J.kg-1.K-1 | G | L3 | Modified Ashrae sizing equation -B (monthly) | 91.5 | 1.592 | 0.104 | 94.7 | 0.22633 | 0.113 | 86.5 | 2.4795 | 0.104 | 90.1 | 1.1629 | 0.113
| 8 | 31 | 291943 | 36 | 437 | 7 | 45 | 1 | 100002.6135 | 8 | -108985.5884 | -556956.0802 | 7 | 33997.555 | 1 |  |  | μf | 0.00337 | kg.s-1.m-1 | H | L3 | Alternative method (monthly) | 88.6 | -1.6279 | 0.1 | 92.1 | -2.5254 | 0.113 | 82.9 | -1.7856 | 0.1 | 86.7 | -2.6546 | 0.113
| 9 | 30 | 97695 | 3751 | 253 | 2 | 84 | 6 | 100002.6135 | 9 | -36243.8272 | -322448.2569 | 2 | 63462.1027 | 6 |  |  | kf | 0.468 | W.m-1.K-1 | Hst | L3 | Alternative method (monthly,short-term effects) | 87.9 | -2.4051 | 0.1 | 91.1 | -3.5838 | 0.113 | 81.7 | -3.2072 | 0.1 | 85.1 | -4.451 | 0.113
| 10 | 31 | 39942 | 32278 | 323 | 3 | 317 | 1 | 100002.6135 | 10 | -2861.4098 | -411663.1897 | 3 | 239493.8875 | 1 |  |  | ρcp,g | 2877 | kJ.m-3.K-1 | I | L3 | EED monthly v.4.17 | 92.6 | 2.8133 | 0.11 | 93.6 | -0.93787 | 0.113 | 86.9 | 2.9534 | 0.11 | 88 | -1.195 | 0.113
| 11 | 30 | 680 | 155203 | 64 | 2 | 322 | 2 | 100002.6135 | 11 | 59615.3549 | -81567.9385 | 2 | 243271.3936 | 2 |  |  | ρcp,gr | 3900 | kJ.m-3.K-1 | J | L3 | GLHEpro monthly v 5.0 | 88.86 | -1.3392 | 0.101 | 93.22 | -1.34 | 0.113 | 82.5 | -2.2595 | 0.101 | 87.2 | -2.0932 | 0.113
| 12 | 31 | 0 | 298351 | 30 | 2 | 373 | 4 | 100002.6135 | 12 | 111391.5024 | -38234.9712 | 2 | 281801.956 | 4 |  |  | ρcp,pipe | 1540 | kJ.m-3.K-1 | K | L4 | EED hourly v.4.17 | 92.2 | 2.3692 | 0.11 | 93.2 | -1.3612 | 0.113 | 86.1 | 2.0056 | 0.109 | 87.3 | -1.9809 | 0.113
[9 empty] | 100002.6135 | [8 empty] | αg | 0.068 | m2.day-1 | L | L4 | DST | 92.9 | 3.1464 | 0.108 | 94.5 | 0.014654 | 0.113 | 86.8 | 2.8349 | 0.108 | 88.9 | -0.18446 | 0.113
| Month | Number of days | Ground monthly cooling averaged load | Ground monthly heating averaged load | Ground monthly cooling peak Load | Peak cooling hours | Ground monthly heating peak load | Peak heating hours | 100002.6135 | [8 empty] | kg | 2.25 | W.m-1.K-1 | X |  | Your tool
[9 empty] | 100002.6135 | [8 empty] | kgr | 1.73 | W.m-1.K-1
[9 empty] | 100002.6135 | [8 empty] | Tg | 12.41 | °C
[9 empty] | 100002.6135 | [8 empty] | kp | 0.45 | W.m-1.K-1
[9 empty] | 100002.6135 | [8 empty] | TL | 4.4 | °C
|  | (days) | (kW) | (kW) | (kW) | (hr) | (kW) | (hr) | 100002.6135 | [8 empty] | TH | 35 | °C |  |  | Mean | 90.0662 |  | 0.10392 | 94.4862 |  |  | 84.4071 |  | 0.10357 | 89.0643
|  |  | qm,C | qm,H | qh,C | th,C | qh,H | th,H | 100002.6135 | [8 empty] | Rb | 0.113 | m.K.W-1 |  |  | Min | 85 |  | 0.1 | 91.1 |  |  | 79 |  | 0.1 | 85.1
Converting buidling and ground loads | 1 | 31 | 0.0041069 | 100.0067 | 57.3525 | 2 | 395.1271 | 11 | 100002.6135 | [8 empty] | t | 10 | years |  |  | Max | 92.9 |  | 0.11 | 108 |  |  | 86.9 |  | 0.11 | 102
| 2 | 28 | 0.017774 | 77.6414 | 21.6665 | 1 | 375.4841 | 5 | 100002.6135 | [8 empty] | Rc | 0 | m.K.W-1
| 3 | 31 | 1.7645 | 39.5583 | 112.1559 | 1 | 374.7286 | 2 | 100002.6135 | [8 empty] | hconv | 1000 | W.m-2.K-1
| 4 | 30 | 7.1296 | 16.8345 | 147.8419 | 2 | 200.2078 | 3 | 100002.6135 | [8 empty] | q''g | 0 | W/m2
| 5 | 31 | 37.568 | 2.407 | 351.7617 | 2 | 108.7922 | 1 | 100002.6135 | [8 empty] | Fsc | 1.04 | -----
| 6 | 30 | 81.0949 | 0.038966 | 563.3286 | 3 | 50.6186 | 1 | 100002.6135 | [8 empty] | COPC | 3.643 | -----
| 7 | 31 | 105.1019 | 0.0011201 | 535.2896 | 5 | 46.8411 | 1 | 100002.6135 | [8 empty] | COPH | 4.09 | -----
| 8 | 31 | 108.999 | 0.013441 | 556.9561 | 7 | 33.9976 | 1 | 100002.6135
| 9 | 30 | 37.691 | 1.4471 | 322.4483 | 2 | 63.4621 | 6 | 100002.6135
| 10 | 31 | 14.9126 | 12.0512 | 411.6632 | 3 | 239.4939 | 1 | 100002.6135
| 11 | 30 | 0.26235 | 59.8777 | 81.5679 | 2 | 243.2714 | 2 | 100002.6135
| 12 | 31 | 0 | 111.3915 | 38.235 | 2 | 281.802 | 4 | 100002.6135
100002.6135
| Month | Number of days | Ground monthly net averaged load | Ground monthly cooling peak Load | Peak cooling hours | Ground monthly heating peak load | Peak heating hours |  | 100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
|  | (days) | (kW) | (kW) | (hr) | (kW) | (hr) |  | 100002.6135
|  |  | qm | qh,C | th,C | qh,H | th,H |  | 100002.6135
Final loads used in comparison | 1 | 31 | 100.0026 | 57.3525 | 2 | 395.1271 | 11 |  | 100002.6135
| 2 | 28 | 77.6236 | 21.6665 | 1 | 375.4841 | 5 |  | 100002.6135
| 3 | 31 | 37.7938 | 112.1559 | 1 | 374.7286 | 2 |  | 100002.6135
| 4 | 30 | 9.7049 | 147.8419 | 2 | 200.2078 | 3 |  | 100002.6135
| 5 | 31 | -35.1609 | 351.7617 | 2 | 108.7922 | 1 |  | 100002.6135
| 6 | 30 | -81.0559 | 563.3286 | 3 | 50.6186 | 1 |  | 100002.6135
| 7 | 31 | -105.1008 | 535.2896 | 5 | 46.8411 | 1 |  | 100002.6135
| 8 | 31 | -108.9856 | 556.9561 | 7 | 33.9976 | 1 |  | 100002.6135
| 9 | 30 | -36.2438 | 322.4483 | 2 | 63.4621 | 6 |  | 100002.6135
| 10 | 31 | -2.8614 | 411.6632 | 3 | 239.4939 | 1 |  | 100002.6135
| 11 | 30 | 59.6154 | 81.5679 | 2 | 243.2714 | 2 |  | 100002.6135
| 12 | 31 | 111.3915 | 38.235 | 2 | 281.802 | 4 |  | 100002.6135
100002.6135
| Month | Number of days | Ground monthly net heat extractionenergy | [5 empty] | 100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
|  | (days) | (kWh) | [5 empty] | 100002.6135
|  |  | qm × tm | [5 empty] | 100002.6135
Determination of the annual ground load imbalance | 1 | 31 | 74401.9444 | [5 empty] | 100002.6135
| 2 | 28 | 52163.0556 | [5 empty] | 100002.6135
| 3 | 31 | 28118.6111 | [5 empty] | 100002.6135
| 4 | 30 | 6987.5 | [5 empty] | 100002.6135
| 5 | 31 | -26159.7222 | [5 empty] | 100002.6135
| 6 | 30 | -58360.2778 | [5 empty] | 100002.6135
| 7 | 31 | -78195 | [5 empty] | 100002.6135
| 8 | 31 | -81085.2778 | [5 empty] | 100002.6135
| 9 | 30 | -26095.5556 | [5 empty] | 100002.6135
| 10 | 31 | -2128.8889 | [5 empty] | 100002.6135
| 11 | 30 | 42923.0556 | [5 empty] | 100002.6135
| 12 | 31 | 82875.2778 | [5 empty] | 100002.6135
Annual load (kW) |  |  | 1.7631 | [5 empty] | 100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
100002.6135
395127.1394
395127.1394
395127.1394
395127.1394
395127.1394
395127.1394
395127.1394
395127.1394
395127.1394
395127.1394
395127.1394
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
77623.59
375484
375484
375484
375484
375484
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
37793.83
374729
374729
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
9704.86
200208
200208
200208
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-35160.92
-351762
-351762
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-81055.94
-563329
-563329
-563329
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-105100.81
-535290
-535290
-535290
-535290
-535290
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-108985.59
-556956
-556956
-556956
-556956
-556956
-556956
-556956
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-36243.83
-322448
-322448
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-2861.41
-411663
-411663
-411663
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
59615.35
243271
243271
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
111391.5
281802
281802
281802
281802

## Test3
Test 3 | Sizing of 7x7 bore filed based on an unbalanced ground load for a ten year period with one peak duration (6 hours) | [14 empty] | Peak load duration of 6 hours | [5 empty] | Effects of spacing and design period
[16 empty] | Rb calculated by tool |  |  | Imposed Rb |  |  | 1 yr, Imposed Rb |  |  | 10 yr, Imposed Rb
Hourly Ground Load |  | Month | Ground monthly averaged load | Ground monthly cooling peak Load | Peak cooling hours | Ground monthly heating peak load | Peak heating hours |  | Ground yearly, monthly and hourly pulses | Parameter | Value | Units |  | Level | Sizing tool | Borehole length | Difference from mean | Rb calculated by tool | Borehole length | Difference from mean | Imposed Rb=0.1 m.k.W-1 | B=3 m | B=5 m | B=7 m | B=3 m | B=5 m | B=7 m
(W) |  |  | (W) | (W) | (hr) | (W) | (hr) |  | (W) | Nb | 7×7 | ---- |  |  |  | (m) | % | (m.K/W) | m | % | (m.K/W) | m | m | m | m | m | m
qh |  |  | qm | qh,C | th,C | qh,H | th,H |  | Cooling | B | 5 | m | A | L2 | Classic ASHRAE sizing equation | 110.7 | 2.2761 | 0.12 | 101.9 | 2.1803 | 0.1 | 116 | 114.6 | 114.3 | 79.6 | 101.9 | 107.9
137920 |  | 1 | 105374.0822 | 0 | 0 | 238670 | 6 | qh | -331000 | D | 2.5 | m | B | L2 | Modified ASHRAE sizing equation | 98.6 | -8.9031 | 0.125 | 87.9 | -11.8582 | 0.1 | --- | --- | ---- | 77.4 | 87.9 | 95.3
144000 |  | 2 | 91741.3562 | 0 | 0 | 214170 | 6 | qm | -150538.1096 | rb | 75 | mm | C | L2 | Modified + ASHRAE sizing equation -B | 100.8 | -6.8705 | 0.12 | 92.4 | -7.3459 | 0.1 | 114.2 | 113.2 | 112.8 | 79 | 92.4 | 99.2
151500 |  | 3 | 55245.2877 | -52830 | 6 | 181170 | 6 | qy | -7712.121 | rp,o,rp,i | 16.7, 13 | mm | D | L2 | Modified + ASHRAE sizing equation- F | 101 | -6.6858 | 0.12 | 92.6 | -7.1453 | 0.1 | 114.2 | 113.2 | 112.8 | 79.3 | 92.6 | 99.4
157750 |  | 4 | 50.8219 | -188500 | 6 | 107330 | 6 |  | Heating | 2dp | 75 | mm | E | L2 | Alternative method | 95.9 | -11.3977 | 0.12 | 87.2 | -12.5602 | 0.1 | 106.4 | 106 | 107.7 | 78.3 | 87.2 | 94.6
162750 |  | 5 | -65165.0274 | -240170 | 6 | 80420 | 6 | qh | 238670 | mf | 33.1 | kg.s-1 | Est | L2 | Alternative method (short-term effects) | 94 | -13.1531 | 0.12 | 85.9 | -13.8637 | 0.1 | 105 | 104.6 | 106.3 | 77 | 85.9 | 93.2
167000 |  | 6 | -122411.1096 | -328170 | 6 | 0 | 0 | qm | 105374.0822 | ρf | 1026 | kg.m-3 | F | L2 | GHX design tool box | 123 | 13.6401 | 0.121 | 115 | 15.3163 | 0.1 | 115 | 115 | 115 | 115 | 115 | 115
168250 |  | 7 | -150538.1096 | -331000 | 6 | 0 | 0 | qy | -7712.121 | cp,f | 4019 | J.kg-1.K-1 | G | L3 | Modified Ashrae sizing equation -B (monthly) | 123.2 | 13.8249 | 0.12 | 114.2 | 14.5141 | 0.1 | 124.6 | 114.2 | 113.8 | 124.6 | 114.2 | 113.8
109330 |  | 8 | -103258.0274 | -307000 | 6 | 0 | 0 |  |  | μf | 0.00337 | kg.s-1.m-1 | H | L3 | Alternative method (monthly) | 120.1 | 10.9608 | 0.12 | 111.1 | 11.4056 | 0.1 | 122.1 | 111.1 | 110.7 | 122.1 | 111.1 | 110.7
98330 |  | 9 | -51052.9178 | -257830 | 6 | 57080 | 6 |  |  | kf | 0.468 | W.m-1.K-1 | Hst | L3 | Alternative method (monthly,short-term effects) | 118.2 | 9.2054 | 0.12 | 109 | 9.2998 | 0.1 | 120 | 109 | 108.5 | 120 | 109 | 108.5
91000 |  | 10 | 4382.2329 | -170670 | 6 | 111500 | 6 |  |  | ρcp,g | 2592 | kJ.m-3.K-1 | I | L3 | EED monthly v.4.17 | 93.4 | -13.7074 | 0.112 | 87.8 | -11.9585 | 0.1 | 122 | 112 | 111 | 83.7 | 87.8 | 97.7
88830 |  | 11 | 50366.0274 | -50670 | 6 | 150670 | 6 |  |  | ρcp,gr | 3900 | kJ.m-3.K-1 | J | L3 | GLHEpro monthly v 5.0 | 118.81 | 9.769 | 0.122 | 109.56 | 9.8613 | 0.1 | 124 | 109.6 | 108.5 | 124 | 109.6 | 108.8
86750 |  | 12 | 92719.9315 | 0 | 0 | 198000 | 0 |  |  | ρcp,pipe | 1540 | kJ.m-3.K-1 | K | L4 | EED hourly v.4.17 | 93.2 | -13.8922 | 0.112 | 87.2 | -12.5602 | 0.1 | 125 | 112 | 111 | 84 | 87.2 | 97.6
87170 | [9 empty] | αg | 0.075 | m2.day-1 | L | L4 | DST | 124.4 | 14.9336 | 0.112 | 114.4 | 14.7146 | 0.1 | 130.625 | 114.4 | 113.8 | 130.625 | 114.4 | 113.4
78580 | [9 empty] | kg | 2.25 | W.m-1.K-1 | X |  | Your tool
75580 | [9 empty] | kgr | 1.73 | W.m-1.K-1
74500 | [9 empty] | Tg | 10 | °C
96580 | [9 empty] | kp | 0.4 | W.m-1.K-1
109670 | [9 empty] | TL | 0 | °C
112670 | [9 empty] | TH | 35 | °C |  |  | Mean | 108.2364 |  | 0.11886 | 99.7257 |  |  | 118.3942 | 111.4538 | 111.2462 | 98.1875 | 99.7286 | 103.9357
126170 | [9 empty] | Rb | 0.1 | m.K.W-1 |  |  | Min | 93.2 |  | 0.112 | 85.9 |  |  | 105 | 104.6 | 106.3 | 77 | 85.9 | 93.2
140000 | [9 empty] | t | 10 | years |  |  | Max | 124.4 |  | 0.125 | 115 |  |  | 130.625 | 115 | 115 | 130.625 | 115 | 115
147170 | [9 empty] | Rc | 0 | m.K.W-1
153330 | [9 empty] | hconv | 1000 | W.m-2.K-1
155580 | [9 empty] | q''g | 0 | W/m2
163330 | [9 empty] | Fsc | 1.04 | -----
164920 | [9 empty] | COPC | ----- | -----
165830 | [9 empty] | COPH | ----- | -----
167080
167920
168250
165920
103080
84420
72580
64080
61750
58750
44080
34080
31000
54170
64420
68750
85000
100250
108580
116670
120080
128920
132420
135250
137670
139750
142330
142580
79330
62580
54080
51420
47750
45500
33250
26000
25750
51830
63830
68580
86750
103170
112500
121000
124750
133000
135830
138080
139330
140500
141670
140500
80000
70080
61920
56420
55170
53920
42670
37920
35670
55330
65670
66750
78420
90170
95670
100580
101420
107080
107920
108580
108750
109420
109830
107750
45330
32330
20080
19330
18080
17830
17580
12420
15830
30750
44830
52330
70830
88420
99080
108330
113250
123000
128750
134330
138330
142500
147330
148670
86920
75000
64830
61250
60170
58830
47330
46000
46000
69580
85330
91000
106170
121920
131000
138580
141670
150250
153080
154920
156670
158420
160420
160080
97170
89170
82830
82420
81330
80080
70250
62330
59000
77580
82670
81750
91170
100500
103670
106500
105330
109080
107580
105580
103580
101670
98000
93750
36330
25580
20750
12580
7250
13170
0
0
0
10670
22000
29250
48000
65670
76080
86250
91500
101920
107080
112080
116750
121080
124920
126420
65420
58420
52500
49750
46920
48670
40580
37330
36830
61500
77750
83000
96670
112670
120830
128330
131580
139420
142420
144420
145920
147250
148330
147500
83920
74750
66500
62170
59830
59000
47830
42920
40580
62920
76670
77670
90750
103080
109330
114750
115500
121670
122500
122750
122750
122000
120830
117750
60580
44420
35920
33330
32920
25000
15750
16250
18500
26250
40170
47250
64080
80420
89420
98580
102580
111500
114750
117080
118580
120170
121420
120330
61420
50000
42580
40830
38170
36500
27750
24750
24920
40170
52000
54500
67170
79920
86170
93420
97830
106500
109750
113170
117000
120420
124420
126420
64170
53330
41920
43750
46830
50000
48500
46670
50000
82330
105920
117250
138420
159830
173670
185920
193670
206170
212580
218330
223000
227170
231080
232830
168670
161080
152080
152420
149250
149580
139420
134750
128420
154250
169830
173920
188750
203830
211670
219170
222000
230500
232830
234580
236420
237580
238670
237500
171250
159330
143170
137580
129750
126670
114920
106830
105920
131170
148250
153080
169170
185000
193420
202000
206330
215250
218250
221080
223330
226330
229080
229330
164170
145830
130580
126330
122500
119420
105420
96580
93250
120830
136920
144170
160330
175670
184330
192000
194750
202500
205170
206750
207920
209670
210500
208500
144170
132670
123830
120170
113580
106330
92170
85000
84920
108170
122000
125500
140670
155330
162670
170500
174420
182750
185750
187580
190920
191750
192420
191580
129500
112670
97500
91330
86830
84750
73330
66580
66920
88330
102830
105750
119330
132830
139000
144580
146250
152670
153420
153670
153500
153170
152750
150420
90080
76580
67250
64580
62420
61330
51750
47250
45580
64000
75000
76580
87830
100830
109580
117250
120420
129420
133500
136830
140250
144170
148170
150330
87830
71420
59580
59080
58420
57580
45920
38670
44670
66580
82080
88170
103250
116830
125170
132500
134080
142000
141330
141670
141920
141580
140170
136830
86000
60000
55580
53500
47420
42670
29920
29080
25330
39580
55750
61250
77420
94500
104830
114830
120000
131170
137080
142080
146750
150920
155000
156830
94000
86920
79830
80000
80170
80750
73500
72250
73670
97000
113580
116420
132330
147500
155750
163330
166170
174080
176330
177920
179080
180000
180330
178670
115330
104250
98330
98000
95170
93170
82750
77170
73670
92420
103170
102330
113750
123420
127750
130830
130170
134750
133830
132250
130420
129750
129000
125250
61920
48830
41080
35750
29250
25750
14170
9670
9670
25000
39500
43170
62500
81750
91830
102000
108170
118580
122920
127420
130080
133080
135330
135580
74250
64420
56500
55250
53830
56420
48920
46330
43750
61830
74330
76830
87830
99830
104670
108830
109000
114170
113750
112920
112920
113250
112580
109920
46330
35500
27080
0
0
0
0
0
0
0
0
42670
59330
76580
87080
97830
104420
115580
122000
128250
133670
138920
143920
146920
85170
76330
69330
68750
66500
65500
54920
49080
44830
65830
82250
86170
100670
116750
125420
133670
138750
149420
155170
160170
164750
170080
175750
178000
110920
95670
84750
81580
82080
81080
68170
63500
59330
82670
103830
113920
135420
156250
168000
178250
183170
192580
195830
198420
200000
200750
202000
200580
144170
108250
98000
91670
87920
83420
67750
60830
54000
74920
89670
94330
111750
127420
135830
143000
145830
154000
156080
157500
159500
161500
162330
161420
98000
85580
76420
64080
60580
57420
44000
33500
30500
50500
64250
68500
90250
109670
121080
130750
134420
142170
143170
143170
143750
141750
139670
135750
84250
64000
50080
42420
34170
29830
17420
12920
15080
23920
32750
34080
50420
64670
72170
78500
80750
87670
90000
90670
91920
92830
93580
92250
31170
26580
24750
20080
0
0
0
0
0
0
0
35170
47830
61330
68250
73580
75250
82080
83830
84580
85330
86420
87080
86250
31170
29580
28000
25420
21420
27580
28750
29170
30920
44830
61580
68330
87170
105920
118000
129420
135830
147750
153330
159000
164000
168750
173170
175500
113080
107420
96250
91000
90920
91420
78920
72420
68670
90830
114920
126580
147670
167420
179830
190420
196830
206580
209330
211250
212420
214000
214170
212420
158920
131670
123750
117080
112170
107750
96420
84750
74580
88000
105250
107080
120580
136330
143580
150000
152500
158920
160420
161500
161750
161500
161330
158670
106830
78420
74500
70250
60000
53420
47330
35750
30920
45500
60000
64500
78920
92170
99420
106830
109500
117920
122250
124500
127670
131830
134830
134750
74250
65830
61920
59000
55080
47250
34170
25750
21000
40170
51080
55750
69750
86000
94580
101920
105000
113330
116080
117500
119330
124580
129250
129920
68580
52420
39420
38420
38420
32080
18170
13420
11250
27170
38830
40750
59080
77670
87330
95920
100170
110080
113750
116750
119750
122500
125170
126170
62580
50330
43330
38920
34920
34830
29170
25330
22000
41750
56080
59830
74080
88750
96330
102420
104000
111500
114080
115420
116000
116580
117250
115250
56830
44330
33750
33330
33920
32670
26330
25330
25330
37920
49580
52000
63330
75420
81420
87670
88920
95250
96080
96750
96920
97000
97000
95170
33920
27750
24670
19830
0
0
0
0
0
0
0
16670
49250
66580
76500
86000
91330
102080
107500
112250
117330
121750
126670
129330
67920
60670
51080
44170
43500
42920
32000
25080
24920
46250
63170
70500
94250
114830
127420
138250
144330
155500
160580
165670
170330
174670
179670
181750
119170
104000
89500
86500
87500
86580
72750
66580
61580
82920
104330
114580
135170
154670
165250
175670
181920
192170
197420
200830
204000
207170
209670
210330
136330
122170
108670
102830
102170
100080
84500
75670
68420
87830
104750
112420
129420
147920
157080
165830
170330
178920
184330
187750
190250
192580
195420
196170
131170
122000
115830
114330
111670
110500
101420
97420
94330
114000
125000
125920
137830
149920
155500
160250
160750
167670
169250
169420
169920
170420
170830
169080
104170
90580
74830
68000
64670
60000
45830
36170
33250
53330
66670
69830
92170
109920
120000
129330
134250
143750
147170
149750
151920
153580
155250
154670
94080
81830
73670
70330
63580
56830
43580
32920
27420
45080
55250
59250
79920
96250
106330
116500
122170
131580
135580
138830
141580
144080
146170
146580
80830
68830
59170
55250
48500
43750
36000
30330
29080
42500
54080
54170
66250
80500
86000
91170
92750
99330
100670
101750
102080
102420
102670
102830
41670
32000
0
0
0
0
0
0
0
0
0
44500
64670
87830
102330
115920
123830
137080
145080
150920
156580
162250
167000
169330
95250
84420
70170
72080
69330
66580
52000
43170
39920
60750
74750
78000
97670
115170
125080
132670
137750
148830
152080
155330
157670
159330
161500
161500
91920
75580
62000
58750
55830
52670
40000
30750
26250
45500
58000
62080
83250
100750
110920
119670
124250
133170
135920
137920
138920
139670
139830
137920
88000
62170
58750
55080
51830
47420
35080
30750
26420
37750
50750
52580
65420
75420
81500
87670
91000
101580
106670
110830
115330
120580
125830
129000
60420
47330
40170
41500
38830
40670
34670
32750
26500
47000
64500
71250
93000
112500
123330
133330
138580
148420
152080
155500
158250
160080
161830
161920
98830
83750
67750
63420
61500
59500
50250
47580
46500
71670
88080
93420
109750
125830
135080
143420
146670
156420
160080
162750
164920
166830
168750
168250
103500
84250
73420
68420
63830
60330
46500
42420
40420
55000
72580
80830
99000
117920
129500
141420
148580
160920
168170
175000
182500
189580
195330
198920
128000
111250
100420
95670
95420
93420
78670
71250
65170
85250
103000
112000
131000
147830
157500
166330
170250
179250
182580
185330
188000
189500
193750
194580
122750
105920
94580
88580
88330
81580
68580
65500
62080
82170
94670
93670
106920
120580
126330
132750
134420
141250
142750
143750
144330
145080
145580
143920
79330
67500
56670
52250
48250
44170
39000
34920
31000
46750
62670
67000
81170
95170
102830
109750
112330
119920
122170
123830
125500
127080
128580
127500
58500
46000
35170
31500
26580
21420
9920
5670
8170
20330
31500
33830
51330
71080
82170
91080
97750
108000
112670
116830
120000
123000
125500
126330
62500
49920
41000
25830
0
0
0
0
0
0
0
16670
54250
70920
80920
89670
94250
105080
109420
112000
114830
117250
119830
119080
58500
43330
33500
31080
25750
17000
9500
11330
9500
13920
24250
30080
45250
59500
67080
77920
82420
91920
95080
98830
103500
107500
111170
113170
45500
34250
26000
0
0
0
0
0
0
0
27580
34420
48830
68920
83420
96170
103000
115580
123580
130580
136920
143170
149170
151080
80830
67750
57580
56920
53750
53000
41580
33170
28920
48500
62170
68500
88080
109500
123170
134920
141500
153500
159920
166670
172170
176500
179830
181170
107080
94330
82170
79080
73170
69500
54750
44170
39000
55750
66670
70750
89000
109670
120920
129750
136170
148170
154830
158830
163500
167330
170920
170000
98670
82830
75080
70080
66000
62080
49250
39170
33750
51170
63330
67830
84500
103580
115000
125330
130250
140000
144420
147420
151000
153330
155250
156250
92170
80830
70330
60670
54420
52920
46420
40830
36580
56420
69330
72750
86080
101750
111170
118920
123420
131750
135920
139750
142500
144750
147750
145580
82580
70750
60830
55580
46080
42830
32750
26000
23000
34080
45250
51000
65250
79920
88420
95170
98080
106500
108830
111080
112330
113830
114920
113580
49500
37830
29170
0
0
0
0
0
0
26420
40670
45500
60750
75830
85000
93580
97920
108000
111920
115000
118500
122000
125420
124500
58330
46580
32500
30830
29670
29170
14000
9500
14170
31920
48670
58330
76250
94330
105500
115250
120330
130420
134580
137750
140580
143170
145500
144000
79080
67580
57500
50170
43170
42670
25080
20250
31250
44170
59330
63170
78000
92500
100420
107500
109830
117330
119250
120670
121580
122000
122500
119830
56500
45670
36830
32170
27420
30000
25250
9500
9500
23920
37250
41250
55250
69420
77080
83750
86330
94080
96080
97670
99080
100000
100920
98670
34750
24830
24830
20000
12330
7580
7250
-21830
-34670
170
10830
16170
29830
46420
57670
66920
71670
80920
85330
88750
91330
93750
96750
95750
31080
21250
17170
7670
6420
9670
-22500
-37170
-49330
-20500
-2670
7080
21580
35750
47250
58170
63500
73500
78170
81920
84580
86830
90670
90750
23080
15830
13750
6920
-9830
-5500
-34500
-42670
-50000
-20000
-14170
4500
19580
35080
49330
62750
69250
80830
87000
91500
95670
99500
102750
101500
39330
31420
26830
23250
20420
26080
25250
25250
25250
28580
42420
46500
60830
74920
82580
89580
92080
99920
102170
103580
104750
106080
106500
105670
42830
31750
25250
23000
18330
10750
9500
9500
-12670
11080
19830
26170
40750
56330
66580
75250
79500
88420
92000
94920
97500
99080
100830
98170
37920
25670
16830
7170
7080
10170
-15670
-16670
-25670
2170
4580
12080
29170
44330
53080
61000
64500
73170
75750
79080
82250
83750
85750
84920
25170
16920
6080
3250
-18330
-17170
-27670
-24000
-20330
-2170
-7330
-330
15830
33580
43420
52250
56000
64500
67500
69580
71330
73000
74170
73420
23080
7670
5580
4250
1750
330
-22000
-21170
-20170
3080
12250
19670
33920
48330
56330
63500
66670
74830
77830
79580
80920
83170
85420
85000
27920
25250
8330
18580
9330
18580
4580
-2170
-20170
9830
20500
24920
39500
55330
64080
72330
76080
85170
88250
90170
92830
95330
97250
89750
24080
12330
9330
4080
-12830
-7330
-33830
-40500
-40330
-21670
-18670
-7000
9830
26000
37920
49080
54500
64580
68830
72000
74750
76830
78920
76000
19170
-2000
-23000
-29170
-27670
-34330
-49170
-52830
-44670
-15500
-9500
-5500
-4170
-1170
14830
28830
33500
43670
48920
53580
56500
59420
62170
62000
6500
3580
4420
4500
1920
3920
2830
5330
4670
9170
19250
27170
42000
57330
65250
72250
75330
83420
86250
88080
89580
91000
91830
90080
29580
25330
23330
18670
9330
18750
-13170
-16170
-19670
8330
23500
27670
43080
58250
66750
75000
78750
87330
90830
94500
99000
102000
104170
103920
39080
26330
16580
10920
11830
11580
7830
5580
-22330
4170
13580
20670
36750
54000
66750
76830
81580
92080
96750
100080
104000
107830
110420
102420
35330
22330
15080
11500
7080
500
-3170
-37830
-48000
-18170
-500
6170
19830
34580
46080
56920
62250
72080
76250
79330
81920
84000
85830
85330
25920
23420
23330
18670
11670
18670
7670
6670
-18500
5000
19000
24750
40330
57920
68420
77580
83250
93580
97580
101500
104920
108330
111500
110420
37750
26920
16750
17580
16250
9670
6670
6000
-25500
5000
15830
23580
40250
57670
71750
83080
89080
100080
104830
108500
111920
115080
117920
116250
49830
40500
31330
30080
22500
22920
5500
2580
580
8830
22170
28830
44750
62830
76500
87920
94580
106080
111670
116080
119830
123250
126170
118830
52330
39500
28580
26920
20330
17250
8500
15580
15920
20250
33420
38170
53000
66920
74500
81580
84080
91420
93500
94500
95250
95920
96670
95080
33420
25500
23420
18750
3670
8750
-25000
-37500
-46000
-16500
-6670
5250
21670
38420
51250
64080
72250
84750
91000
97420
103330
108830
113080
107330
42000
32500
22170
21750
16330
13080
4000
3670
80
4670
14580
20420
36080
53580
65920
75830
80670
90170
94000
97000
99250
101080
102330
98920
34420
21500
8420
8420
4000
2420
-24000
-38000
-40330
-10330
-2830
-4170
6500
21580
35330
44500
49080
58500
61670
64920
68080
71250
73250
73080
22830
7750
6500
5330
2250
6170
4830
4000
4170
13000
23330
27420
41750
56080
63750
70670
73670
81420
83420
85580
87920
89580
90580
81580
16500
9920
7500
-6000
-16330
-30000
-46670
-50330
-52670
-32170
-27500
-14170
3420
16000
30250
43170
52000
63750
69580
74330
78000
81670
84170
82250
23420
19580
8250
6920
-17170
-28670
-51500
-59330
-61000
-40000
-29670
-17330
-8330
-6830
8330
23420
30830
44000
51580
58080
63830
69170
73920
66580
15420
-10670
-30330
-31500
-30330
-32670
-49830
-52830
-55170
-34330
-26830
-15000
-5000
6420
24500
39500
47580
59330
67080
73000
78080
82580
85580
78420
19500
11670
2670
-5330
-15330
-34000
-46500
-45830
-38830
-13330
-8830
-11000
-7670
1420
17170
30250
34750
43670
47330
49580
51170
52080
53000
50920
11330
-25330
-19830
-16500
-9000
-8000
-39000
-40670
-53670
-32500
-17500
-10830
-11500
-15500
-6170
10500
21920
34330
40670
46250
51250
55580
58750
52330
-6330
-33330
-37330
-39330
-33000
-39000
-57670
-48170
-77500
-48170
-33330
-21000
-7170
-7670
3580
22830
34250
48830
56330
61830
68330
74250
78250
70830
16250
10500
-29000
-29670
-26830
-33000
-45330
-49330
-54500
-34170
-27830
-15500
-6500
3670
19000
32500
41250
53580
59420
64000
68420
72420
74500
66670
15580
-26670
-33000
-36670
-38500
-43170
-77830
-61500
-90330
-57170
-31830
-24670
-5830
-4670
-13500
-8500
-2330
14920
21420
27750
34420
38170
41830
36750
-26500
-24170
-42330
-42000
-59170
-77330
-110500
-134170
-149830
-119500
-97330
-82330
-51830
-21500
-8330
-5500
-9170
-6830
-7830
4500
14330
23750
29500
27080
-26330
-18830
-46500
-58000
-72170
-91830
-121330
-142830
-157830
-122500
-98330
-87330
-63330
-33330
-15500
-4000
-3000
-4500
-11170
-6000
-500
3830
10330
14500
-29000
-11670
-34000
-54170
-58170
-60170
-77330
-86670
-87330
-49830
-27830
-23830
-6670
-3330
-11170
-8000
-3830
8670
13830
19670
22750
25170
26830
25830
-23000
-22330
-26000
-57500
-63000
-88170
-98170
-104330
-104000
-67330
-44330
-36330
-13670
-2330
-7830
-8170
-6830
3830
9000
18080
23920
28250
32170
34500
3670
-7000
-26000
-17170
-13330
-9830
-28670
-26500
-28670
1330
2330
4750
16750
32080
45420
54670
58580
67170
70330
72830
75250
76830
78500
77670
23750
8420
7580
-11670
-7000
-5670
-28670
-38330
-38670
-17170
-13670
-11500
2420
15500
30330
42330
49000
60250
65420
69500
73920
78750
77750
71420
15830
9250
-31330
-30500
-27830
-32170
-49000
-52830
-57500
-37500
-28670
-20500
-10500
-7170
7670
24750
33830
46580
53420
58330
62670
67080
69750
67580
23250
-13500
-15670
-21830
-27330
-39830
-61170
-47670
-65500
-39500
-22500
-14670
-2670
-12170
-16170
750
12420
26500
31670
36330
40080
42830
43750
41830
-19670
-18170
-20170
-16000
-8170
-9670
-31330
-18500
-39670
-9670
-6170
-10330
-170
5580
18170
30580
36250
45500
48580
51830
55080
57830
60080
60170
5080
4250
5170
4250
-7170
-15000
-27330
-20330
-22830
-5830
-2500
3420
18500
35000
45330
53170
56750
65250
68080
70580
72670
74420
74500
73580
22750
7830
-17830
-15500
-4330
-7170
-24000
-18670
-21170
-2330
-10000
-5000
12670
28830
40250
49250
52670
61500
64500
66750
68580
70330
69500
67830
22500
2750
-21000
-12830
-2830
-27330
-52830
-57830
-64830
-43330
-36670
-29170
-13500
-15170
-8330
6670
19170
35170
42830
49830
55500
60580
57580
54170
-4500
-35330
-36670
-33670
-30830
-44670
-64670
-65170
-86170
-53500
-32500
-21330
-5000
-6170
-11500
-1330
8330
25920
32420
37330
41920
45500
48420
47750
3170
-19000
-19170
-14670
-3170
-8170
-28500
-21170
-29170
-9330
-9170
-10500
830
10750
27420
39170
44170
53920
57670
60670
63170
65170
66670
65750
7830
4170
4000
4170
1920
4420
-25830
-19500
-21500
4750
9830
15830
32170
46920
55170
62330
65250
72830
75500
77670
79330
80580
81500
78750
23170
500
-17670
-17670
-24830
-33000
-56830
-53830
-59170
-40330
-28500
-16500
-5330
-11330
-9500
6000
18250
30750
35670
41500
47500
51750
47420
45000
-28170
-38170
-35670
-41170
-38170
-53330
-76170
-90170
-109500
-82000
-61170
-52670
-20670
-4830
-8670
-6500
-4170
11920
19250
24000
27080
29170
30170
25250
-9830
-17170
-57000
-86830
-101500
-128170
-157000
-170330
-188500
-152500
-136170
-126500
-99830
-68670
-53330
-42500
-33500
-20170
-14000
-11500
-7330
-5670
-2170
-12670
-127500
-143000
-155500
-155830
-151500
-145830
-158670
-159830
-153170
-109500
-81000
-68330
-38670
-14670
-4000
-2500
-9170
670
2750
10670
18920
24830
28000
27000
-21830
-8830
-26830
-41330
-44670
-61000
-77330
-89830
-104830
-75170
-53670
-42000
-14500
-4500
-9670
-6830
-2170
13170
23330
29500
34250
37170
37500
33170
-13000
-39330
-47330
-58000
-77330
-86670
-106000
-119670
-126670
-97670
-82330
-77500
-48170
-18670
-5500
-2670
-7170
-2170
-9670
-6500
1330
9420
11920
7080
-44500
-49330
-74330
-109500
-112000
-115500
-129170
-143000
-148170
-107830
-77330
-66830
-39830
-11330
-2170
-7670
-11830
-3500
420
10750
19830
26580
31250
34420
-330
-6830
-25670
-16170
-10670
-17500
-26830
-20670
-21830
3250
-5000
670
16580
34920
47250
55670
59330
69420
72750
75500
78080
80420
80330
69920
14670
1330
-30000
-29830
-29330
-26500
-55670
-44830
-59830
-26500
-13170
-8500
-4000
-15500
-13170
3670
14330
28330
34580
40170
44830
48920
49830
47000
-15500
-18000
-18830
-12500
-36830
-40670
-84000
-94330
-108330
-74000
-48330
-40330
-14830
-2330
-10670
-12330
-9500
1000
5920
17420
23170
27500
26500
22670
-34670
-26000
-55670
-72670
-82830
-93000
-107830
-117170
-122000
-79670
-54000
-46830
-21330
-1670
-2830
-6830
-8670
-1330
3750
14580
18830
22080
24670
22500
-23500
-21330
-42330
-75170
-92670
-104000
-132330
-151500
-163500
-124330
-94670
-81170
-51330
-23830
-8670
-2000
-4670
-4670
-10330
0
5920
13670
19170
21000
-24330
-21170
-34330
-38000
-36670
-41170
-60170
-75330
-81000
-42500
-17330
-13000
-6170
-10500
-11000
1750
10250
24830
29080
34420
40500
44170
41080
37080
-28330
-23670
-44670
-37170
-61830
-69830
-102170
-122170
-137000
-107500
-84500
-72500
-46000
-18000
-2170
-1170
-6670
-6000
-10830
-4000
2170
9000
14580
16500
-26670
-10000
-37830
-43500
-43670
-47170
-65170
-74330
-86170
-49830
-25170
-18670
-4000
-4830
-11830
-6170
1170
14920
22330
27580
31830
35830
32580
27830
-33170
-25830
-49830
-59170
-82170
-91670
-120170
-141830
-156830
-127670
-103500
-91500
-63670
-35170
-16830
-3500
-4330
-6330
-12170
-6330
250
7750
12500
13080
-30330
-38500
-63330
-95330
-100830
-105670
-128170
-142330
-149670
-115170
-89170
-79000
-50830
-24170
-8670
-2000
-5500
-4330
-9500
-5000
-3170
1500
5750
9330
-36500
-18000
-55170
-67830
-96830
-113330
-136830
-141670
-144500
-106670
-81830
-71170
-42670
-15830
-4000
-4330
-7330
-3830
-10170
-110830
-2500
-101670
7750
-97500
-36000
-97500
-49330
-102500
-70500
-113330
-90000
-118330
-102500
-122500
-47170
-113330
-14830
-95000
-7330
-97500
-9330
-79170
9000
-78330
21750
-60000
23080
-85830
-35500
-111670
-55330
-122500
-99830
-130000
-139000
-134170
-162500
-134170
-104670
-123330
-64830
-95000
-13500
-88330
-2170
-85830
-11500
-79170
830
-62500
12080
-95000
-36000
-113330
-88830
-145830
-112500
-176670
-160830
-192500
-200330
-190000
-155830
-176670
-109330
-150830
-60500
-125000
-30500
-118330
-4170
-125000
-4500
-104170
-10170
-97500
-99330
-111670
-141830
-130000
-143170
-155000
-182000
-171670
-211670
-174170
-154330
-160000
-105830
-139170
-57000
-113330
-24000
-102500
-5500
-80830
-8670
-62500
-7170
-83330
-66500
-113330
-98830
-141670
-130330
-162500
-171830
-174170
-201330
-178330
-145330
-166670
-101000
-155000
-53170
-136670
-24330
-134170
-3330
-135000
-1830
-130000
-2830
-134170
-82170
-155000
-142830
-169170
-158500
-164170
-157000
-145830
-153670
-118330
-81330
-115830
-45500
-106670
-7170
-100000
-5330
-93330
-10500
-69170
6920
-62500
13750
-83330
-39500
-109170
-71170
-125000
-111170
-135000
-147500
-150830
-181500
-160000
-130830
-150830
-89000
-122500
-34830
-104170
-11830
-83330
-6500
-78330
-5000
-70000
-3670
-60000
-52500
-74170
-76830
-83330
-109830
-95000
-137000
-109170
-162170
-115830
-100830
-110830
-56830
-104170
-10170
-95000
-4830
-81670
-11670
-74170
3580
-74170
17830
-83330
-20330
-102500
-38330
-90830
-40000
-100000
-59170
-106670
-69830
-95000
-17830
-80830
-2500
-88330
-6000
-95000
13670
-100000
28080
-100000
31830
-106670
32250
-122500
-20830
-141670
-43330
-157500
-103830
-174170
-145500
-178330
-182500
-178330
-137170
-166670
-95170
-143330
-41830
-120830
-15670
-97500
-7500
-70000
-7670
-55830
-9170
-74170
-64500
-102500
-82670
-100000
-102000
-109170
-119000
-118330
-136000
-123330
-76670
-106670
-36830
-95000
-3170
-76670
-8830
-65000
-3330
-49170
17170
-32500
22250
-65000
-21000
-88330
-63000
-106670
-87000
-118330
-124000
-127500
-158500
-130000
-111670
-120830
-67330
-95000
-15500
-80830
-3830
-70000
-10170
-55830
8420
-51670
18830
-80830
-21170
-132500
-57830
-144170
-99330
-157500
-141500
-162500
-177500
-161670
-133330
-155000
-89830
-134170
-36500
-118330
-15000
-88330
-7500
-78330
-6000
-71670
420
-109170
-49000
-150830
-91830
-180830
-138830
-192500
-182830
-201670
-221330
-199170
-174500
-187500
-130670
-145830
-69830
-132500
-40170
-111670
0
0
0
0
0
-132500
-75500
-165000
-135170
-176670
-149670
-190000
-197000
-208330
-240170
-208330
-163330
-200830
-123500
-187500
-77170
-164170
-52670
-123330
0
0
0
0
-10330
0
-110330
-126670
-152170
-144170
-162500
-156670
-193330
-170000
-224670
-166670
-162000
-151670
-114170
-134170
-63170
-117500
-29830
-112500
0
0
0
0
0
0
-85170
-149170
-139500
-171670
-163000
-187500
-204500
-194170
-240000
-199170
-190830
-183330
-143330
-155000
-84330
-141670
-51830
-134170
-18000
-118330
-6500
-117500
-830
-125830
-104500
-147500
-169670
-168330
-179500
-172500
-195000
-175000
-207670
-165000
-133670
-151670
-92830
-146670
-43830
-145000
0
-140830
0
-140830
0
-144170
0
-140830
-84500
-154170
-129000
-163330
-145670
-159170
-176500
-160830
-173330
-169170
-122830
-169170
-84000
-142500
-33500
-134170
0
0
0
0
0
0
0
-127500
-84000
-149170
-148330
-185000
-175330
-210830
-230170
-216670
-268830
-216670
-215670
-196670
-161830
-173330
-103170
-163330
-70830
-162500
-37830
-158330
0
0
0
-144170
-131500
-151670
-168000
-172500
-187670
-190830
-223830
-197500
-250500
-204170
-196500
-157500
-135000
-138330
-76830
-135830
0
0
0
0
0
0
0
-103330
-104500
-117500
-156830
-128330
-160500
-144170
-191500
-154170
-215830
-154170
-167000
-135830
-119000
-109170
-56670
-84170
-21000
-86670
0
0
0
0
0
0
-62330
-124170
-95670
-137500
-123170
-147500
-139670
-150830
-152000
-157500
-92500
-155830
-59000
-158330
-15830
-153330
0
0
0
0
0
0
0
-141670
-69000
-153330
-121170
-168330
-154830
-172500
-188830
-168330
-211170
-160000
-153330
-152500
-108170
-129170
-52830
-101670
-19830
0
0
0
0
0
0
-114170
-77330
-140830
-114830
-147500
-153000
-167500
-195000
-167500
-215330
-167500
-156000
-157500
-113000
-120000
-54170
-125000
0
0
0
0
0
0
0
0
-93170
-145000
-147170
-160000
-165670
-166670
-201170
-176670
-228500
-183330
-175830
-155000
-124330
-122500
-64330
-128330
-33670
-124170
0
0
0
0
0
-134170
-109500
-156670
-166500
-161670
-181670
-173330
-206500
-173330
-204670
-155000
-134330
-130830
-88830
-125830
-38830
-120830
-13830
0
0
0
0
0
0
-127500
-91330
-150000
-131330
-168330
-167330
-176670
-206000
-190000
-240170
-193330
-191000
-184170
-146830
-154170
-83670
-146670
-51670
-141670
-18000
-141670
0
0
0
-150830
-117670
-169170
-180000
-192500
-189500
-182500
-202830
-173330
-215670
-175830
-147670
-162500
-102670
-155000
-54330
-146670
0
0
0
0
0
0
0
0
-95500
-146670
-125670
-156670
-147830
-173330
-177670
-191670
-197500
-205830
-142330
-202500
-103500
-194170
-58000
-189170
-39330
-180000
-17830
-178330
0
0
0
-194170
-160000
-222500
-231830
-235830
-252670
-240000
-299670
-243330
-328170
-249170
-260500
-218330
-204670
-203330
-142830
-202500
-115670
-175000
-76830
-158330
-55670
-145000
-37830
-148330
-155330
-160000
-203330
-183330
-221000
-192500
-254170
-184170
-259170
-186670
-211670
-181670
-166830
-153330
-99670
-125830
-61830
-121670
0
0
0
0
0
-139170
-127000
-161670
-183830
-181670
-201330
-199170
-240500
-210000
-276830
-213330
-224500
-204170
-175830
-180000
-113500
-163330
-81330
-145000
-44170
-142500
0
0
0
-158330
-136670
-186670
-208830
-198330
-232330
-214170
-270330
-217500
-268830
-163330
-177170
-165830
-136830
-168330
-83670
-166670
-55000
-160830
-27500
-153330
-12670
-153330
-8500
-145830
-142170
-168330
-192170
-174170
-207500
-179170
-237170
-187500
-240170
-184170
-171500
-180000
-128830
-161670
-76000
-155000
-54170
-130000
-19830
-112500
0
0
0
0
-114670
-152500
-162500
-165000
-170830
-166670
-196330
-183330
-223670
-181670
-174330
-172500
-128000
-155830
-72330
-140000
-40170
-146670
0
0
0
0
0
-142500
-95000
-134170
-110000
-135830
-106000
-162500
-125000
-174170
-163330
-158330
-99000
-139170
-56670
-134170
0
0
0
0
0
0
0
0
0
0
-78330
-145000
-121170
-158330
-155330
-173330
-194500
-180830
-229330
-180830
-183830
-163330
-139500
-131670
-74670
-126670
-43670
-98330
0
0
0
0
0
0
-94170
-152500
-151670
-168330
-169500
-181670
-201500
-173330
-210000
-170000
-145170
-160830
-103330
-151670
-55670
-138330
-28170
-136670
0
0
0
0
0
-147500
-95830
-162500
-158000
-181670
-188830
-203330
-229000
-210000
-265000
-212500
-203170
-170000
-148830
-145830
-88830
-137500
-56500
-123330
0
0
0
0
0
-118330
-89670
-111670
-103670
-117500
-98000
-122500
-108500
-124170
-125000
-122500
-62830
-122500
-29330
0
0
0
0
0
0
0
0
0
0
-114170
-46000
-148330
-95000
-183330
-140330
-203330
-189330
-212500
-226670
-206670
-184830
-190830
-147000
-150830
-81830
-138330
-50330
-132500
0
0
0
0
0
-137500
-127170
-164170
-185000
-185830
-192830
-205830
-233170
-216670
-268500
-216670
-219330
-199170
-172000
-175000
-111670
-148330
-74330
-139170
-38500
-126670
-19330
-118330
-14330
-155830
-127170
-185000
-186000
-200000
-193670
-215830
-230500
-209170
-255000
-217500
-205000
-205830
-153170
-190000
-98170
-184170
-70830
-177500
-42830
-180000
-29670
-173330
-22330
-177500
-142500
-185000
-184000
-195000
-207170
-219170
-242000
-224170
-267000
-209170
-186330
-172500
-134330
-170000
-83670
-165830
-56330
-161670
-28670
-160000
0
0
0
-166670
-139000
-183330
-180670
-201670
-205000
-201670
-244170
-196670
-229330
-180830
-157330
-175830
-114830
-187500
-69500
-171670
-48830
-130000
0
0
0
0
0
-153330
-109330
-169170
-171000
-180830
-199000
-201670
-236330
-203330
-264830
-194170
-201170
-190000
-160000
-155000
-94500
-141670
-61670
-127500
-26500
-127500
0
-110830
0
-130000
-121170
-150830
-178170
-157500
-184170
-166670
-217000
-175830
-250170
-174170
-194500
-162500
-142670
-136670
-80830
-120000
-44500
-122500
0
0
0
0
0
-120830
-110000
-144170
-164170
-155000
-174170
-176670
-211330
-185000
-240670
-185000
-191830
-171670
-139000
-150830
-81000
-132500
-48330
-120830
0
-104170
0
0
0
-125000
-107500
-150830
-161330
-157500
-152670
-148330
-158170
-157500
-196000
-180830
-142330
-171670
-97170
-150830
-48330
-127500
-20500
-115830
-2670
-118330
0
0
0
-115830
-62670
-130000
-89670
-148330
-132830
-165000
-157330
-166670
-185500
-171670
-148500
-166670
-103330
-144170
-50000
-127500
0
0
0
0
0
0
0
-125000
-64830
-127500
-84000
-136670
-117000
-169170
-164670
-195000
-204500
-199170
-145330
-192500
-104170
-175830
-56670
-169170
-35000
-161670
0
0
0
0
0
-157500
-133170
-176670
-180500
-190000
-206670
-213330
-247500
-229170
-285000
-226670
-231670
-220000
-182330
-196670
-122000
-185830
-90670
-174170
-56000
-171670
-41170
-150830
-33670
-162500
-156330
-196670
-220330
-225000
-251000
-240830
-296500
-235830
-325830
-215000
-241330
-166670
-180500
-169170
-123830
-166670
-88670
-169170
-55330
-148330
-39330
-127500
0
-130000
-137330
-132500
-190670
-141670
-195500
-157500
-227170
-174170
-256170
-174170
-202670
-166670
-154500
-136670
-87330
-132500
-55170
-106670
-18170
-93330
0
0
0
-115830
-108830
-145830
-157000
-171670
-169330
-187500
-205000
-196670
-242670
-201670
-196330
-195000
-152500
-162500
-91500
-145830
-58830
-127500
-22000
-125000
-10830
-120830
-6500
-145830
-120500
-169170
-185670
-195000
-197670
-210830
-240330
-215830
-262000
-215830
-200670
-183330
-153170
-161670
-96330
-161670
-68170
-157500
-37670
-145830
-23000
-130000
-13170
-155000
-136330
-175830
-203830
-190000
-217670
-204170
-254170
-208330
-267670
-208330
-214170
-199170
-166830
-178330
-106000
-180830
-80500
-148330
-45830
-132500
-26170
-130000
-20670
-155000
-138170
-195000
-212000
-218330
-238830
-236670
-292500
-247500
-325500
-247500
-260000
-234170
-205830
-217500
-148330
-201670
-117670
-185000
-83170
-178330
-64830
-174170
-54500
-190000
-187330
-213330
-259330
-231670
-287000
-245830
-329000
-255000
-253330
-247500
-272170
-238330
-221000
-222500
-162170
-213330
-132000
-201670
-98330
-194170
-79500
-190000
-73170
-199170
-217830
-222500
-282170
-240830
-305000
-257500
-260000
-261670
-216670
-234170
-281000
-220000
-229830
-210830
-167670
-205830
-133670
-199170
-99170
-192500
-80500
-180830
-67830
-192500
-202670
-210830
-262830
-229170
-283170
-245000
-321670
-255000
-331000
-259170
-276830
-243330
-223170
-226670
-163170
-213330
-128670
-201670
-97000
-196670
-78000
-192500
-75330
-205830
-220830
-218330
-280170
-240830
-298830
-247500
-283330
-240830
-260000
-234170
-294500
-217500
-229170
-210830
-164670
-196670
-126000
-194170
-91170
-201670
-72830
-201670
-70670
-218330
-211000
-225000
-257000
-229170
-265330
-196670
-260170
-201670
-266000
-196670
-204670
-196670
-161000
-176670
-100000
-166670
-68830
-153330
-40330
-130000
-21500
-113330
-21000
-135000
-134500
-148330
-182000
-169170
-190500
-183330
-224830
-192500
-260170
-194170
-211000
-183330
-160500
-152500
-96170
-141670
-61670
-155000
-28330
-155000
-11170
-144170
0
-143330
-118330
-171670
-182000
-196670
-198000
-208330
-238330
-220000
-273170
-215830
-219830
-204170
-166170
-190000
-109170
-192500
-79830
-185000
-51330
-180830
-37670
-171670
-25330
-180830
-162170
-210830
-223000
-229170
-244170
-243330
-285170
-259170
-323830
-255000
-264500
-238330
-211170
-185830
-142830
-174170
-109500
-155000
-70330
-143330
-46500
-148330
-31170
-150830
-154830
-169170
-204170
-175830
-207670
-190000
-239830
-199170
-266670
-196670
-206170
-180830
-154170
-155000
-94500
-144170
-62170
-134170
-27500
-134170
-11500
-139170
-2000
-144170
-105170
-164170
-142500
-171670
-164170
-175830
-184170
-169170
-183830
-166670
-118330
-161670
-81170
-155000
-35000
-157500
-13830
-157500
-1330
-155000
-5670
-145830
-830
-157500
-96330
-160000
-159670
-178330
-175330
-196670
-215000
-210830
-237000
-210830
-183670
-180830
-137330
-145830
-78170
-135000
-50170
-118330
0
0
0
0
0
-134170
-112000
-169170
-174500
-190000
-190000
-199170
-233170
-208330
-263170
-213330
-209000
-201670
-160830
-175830
-102670
-164170
-70500
-164170
-42830
-143330
0
0
0
-155000
-140670
-176670
-197670
-196670
-213500
-213330
-246330
-215830
-256670
-205830
-181670
-192500
-140830
-166670
-88330
-161670
-60000
-169170
-31670
-164170
-18670
-157500
0
-160000
-131000
-169170
-177170
-180830
-193670
-190000
-224170
-192500
-253000
-187500
-191500
-153330
-143830
-122500
-80000
-122500
-45330
-120830
-18330
-97500
0
-95000
0
-104170
-91500
-127500
-141000
-148330
-147500
-157500
-179000
-162500
-203000
-148330
-148170
-136670
-100670
-111670
-44000
-93330
0
0
0
0
0
0
0
-100000
-64000
-130000
-92000
-144170
-129500
-157500
-170670
-162500
-205500
-171670
-158330
-165000
-113170
-134170
-53670
-125000
0
0
0
-115830
0
-115830
0
-136670
-80000
-178330
-135500
-204170
-169330
-204170
-197500
-217500
-222330
-226670
-154330
-207500
-117000
-198330
-73330
-184170
-52330
-167500
0
-154170
0
-149170
0
0
0
-155000
-169330
-174170
-192170
-196670
-228170
-196670
-254330
-201670
-193170
-187500
-150330
-157500
-88830
-145830
-58330
-136670
0
-127500
0
0
0
-141670
-108170
-169170
-172000
-201670
-188500
-215830
-234830
-220000
-264000
-208330
-191500
-201670
-149000
-185830
-99000
-183330
-71500
-183330
-44330
-178330
-31170
-180830
-22000
-180830
-144670
-187500
-181830
-192500
-217170
-213330
-256670
-220000
-291830
-226670
-211330
-210830
-166330
-178330
-106500
-180830
-78670
-180830
-50000
-180830
-36330
-180830
-26670
-187500
-150830
-199170
-197670
-192500
-186330
-195000
-233830
-210830
-246670
-171670
-163330
-174170
-126000
-178330
-75170
-171670
-50330
-155000
-24000
-134170
0
0
0
-139170
-124170
-160000
-174170
-174170
-191500
-174170
-214500
-229330
-252500
-218670
-191000
-170830
-136830
-100830
-79330
-61000
0
0
0
0
0
0
0
0
-105170
-113330
-161500
-163670
-171170
-180830
-210330
-230000
-244330
-211330
-195000
-189670
-147500
-109000
-82670
-61000
-48500
-29170
0
0
0
0
0
0
-114670
-133000
-177000
-181000
-185500
-206000
-230500
-251500
-265500
-232830
-211000
-194670
-158170
-122830
-100170
-80500
-69170
-49330
-37500
-28670
0
0
0
0
-133830
-155330
-174670
-177670
-184670
-197830
-233330
-254830
-261170
-222330
-193330
-177170
-144500
-112830
-94330
-77170
-68830
-52830
-44330
-34830
-29170
-24670
0
0
-138330
-157500
-175330
-173330
-171830
-174500
-183670
-186330
-187500
-147830
-122500
-115670
-86500
-56000
-41330
-26000
-18830
0
0
0
0
0
0
0
-106830
-122500
-151670
-146830
-147330
-146830
-166830
-178500
-186000
-143500
-115330
-103330
-73000
-43500
0
0
0
0
0
0
0
0
0
0
-54830
-49830
-91000
-108500
-117000
-118330
-146170
-165170
-170330
-127000
-100170
-92830
-63500
-33830
-17830
0
0
0
0
0
0
0
0
0
0
-56170
-102330
-143830
-138000
-145670
-183670
-198330
-202670
-169500
-153170
-151170
-115170
-80670
-61170
-43000
-31830
0
0
0
0
0
0
0
0
-106000
-151830
-162830
-178000
-182330
-211830
-228830
-229830
-191000
-169330
-167000
-132330
-102500
-80670
-60170
-50500
0
0
0
0
0
0
0
-107830
-145500
-173830
-178000
-170330
-194830
-220170
-237500
-242830
-194000
-175330
-158500
-127500
-96330
-74170
-56670
-46330
-30830
0
0
0
0
0
0
-120330
-155830
-181830
-193170
-201170
-210670
-241670
-264830
-279830
-243500
-217500
-205000
-166830
-130830
-108830
-88830
-78170
-58500
-46500
-34830
0
0
0
0
-142170
-177830
-202670
-214500
-225500
-236830
-268170
-289170
-289830
-249670
-216330
-202330
-163000
-129500
-108330
-87330
-78330
-56830
-45670
-35670
-28170
0
0
0
-150500
-184830
-213330
-225330
-234500
-249330
-279170
-297000
-307000
-266500
-235330
-218500
-183670
-149670
-127500
-109170
-98330
-77330
-67670
-59170
-51500
-44170
-40330
-44170
-166830
-185000
-220170
-237000
-229670
-242330
-264670
-280000
-289670
-228000
-185830
-175170
-140170
-107170
-87000
-67000
-56670
-36830
-29000
0
-13830
0
0
0
0
-127330
-144670
-146670
-144500
-143170
-155670
-162670
-171000
-132000
-109830
-99500
-70830
-41170
-23170
0
0
0
0
0
0
0
0
0
-67500
-58500
-97830
-106330
-108830
-111000
-128670
-140000
-145830
-102330
-79170
-72670
-44330
0
0
0
0
0
0
0
0
0
0
0
-79500
-88170
-120830
-158670
-165000
-178330
-210670
-233500
-246500
-211170
-187330
-169830
-134830
-103500
-81000
-60000
-49500
-29500
0
0
0
0
0
0
0
-106670
-121330
-132500
-148500
-151330
-170170
-181830
-199170
-167500
-142000
-122000
-89000
-57170
-37000
-18670
0
0
0
0
0
0
0
0
-60670
-63830
-90000
-124330
-130170
-137170
-169000
-183830
-193330
-152170
-134830
-123330
-89000
-56500
-36000
0
0
0
0
0
0
0
0
0
-47500
-61670
-90500
-125170
-139000
-149830
-177830
-203830
-219000
-185000
-162330
-146330
-110330
-79670
-58670
0
0
0
0
0
0
0
0
-1670
0
-81330
-116170
-154330
-161000
-175000
-206670
-226830
-242500
-207000
-184670
-178330
-138330
-101830
-79670
-61500
-49830
0
0
0
0
0
0
0
-110000
-163830
-191670
-197000
-212000
-220170
-244670
-264170
-269170
-217170
-185830
-174000
-142830
-110670
-91330
-72830
-62500
-43830
-34670
-27830
0
0
0
0
-152170
-174330
-181500
-193830
-212170
-223500
-254330
-267170
-283170
-237330
-202000
-186830
-154330
-119830
-99830
-82670
-74170
-56000
-47500
-39670
-33000
-27000
0
0
-141670
-157000
-163500
-156670
-147330
-146000
-169000
-183670
-186000
-137170
-109500
-99330
-70330
-40830
-24500
0
0
0
0
0
0
0
0
0
-74830
-82000
-139670
-161830
-176500
-187670
-223670
-244830
-256170
-217830
-187000
-172830
-139670
-107000
-89170
-72170
-61000
-41500
-32500
0
0
0
0
0
-117170
-130330
-138170
-151330
-162500
-162000
-167330
-169330
-170830
-130670
-105830
-96330
-65830
-34830
-18830
0
0
0
0
0
0
0
0
0
-35670
-16670
-44670
-53330
-69170
-82670
-99170
-111670
-125500
-92000
-69500
-59330
-28830
0
0
0
0
0
0
0
0
0
0
0
-22670
-29500
-66330
-106500
-127500
-144330
-181500
-208670
-226330
-195000
-173170
-157830
-122170
-86830
-66830
-49500
-38830
-19670
0
0
0
0
0
0
-110170
-138330
-172670
-176170
-181670
-182670
-207830
-213170
-209830
-169670
-140170
-132000
-103170
-74000
-57000
-42330
-36830
-20170
0
0
0
0
0
0
-118000
-140670
-165670
-184830
-197830
-204330
-233830
-249670
-257830
-219170
-190670
-164670
-127170
-91500
-67500
-46000
-33330
0
0
0
0
0
0
0
-65500
-67170
-109330
-127000
-134000
-141500
-167170
-184330
-197170
-165170
-142170
-121330
-85670
-53170
-31170
0
0
0
0
0
0
0
0
0
-61330
-70000
-100670
-137000
-146170
-159830
-191170
-214830
-233830
-200500
-175330
-156500
-120000
-85330
-68830
-50670
-39330
-20500
0
0
0
0
0
0
-110500
-121170
-136830
-133170
-129170
-126170
-139500
-143000
-145000
-104670
-79670
-73830
-47170
0
0
0
0
0
0
0
0
0
0
0
-68000
-71170
-97170
-133670
-132330
-138330
-164830
-183000
-188830
-142170
-112000
-98170
-68170
-37000
-18500
0
0
0
0
0
0
0
0
0
-42000
-42670
-65670
-92830
-88500
-96500
-110000
-113330
-117000
-77830
-53500
-44830
-18670
0
0
0
0
0
10080
20250
25000
28920
30750
27000
-26500
-20330
-52830
-76670
-90000
-102000
-121170
-137000
-142170
-106670
-75330
-63330
-35500
0
0
0
0
0
0
0
14670
19420
22830
23080
-20830
-10330
-26170
-54330
-78170
-77170
-89170
-92500
-98500
-62830
-42000
-36500
0
0
0
0
0
10580
17580
25080
30080
33830
37250
32080
-29000
-29830
-48330
-58670
-77000
-84000
-103000
-123170
-127830
-89500
-72170
-59670
-28670
0
0
0
0
0
0
0
18920
23420
27580
27330
0
0
-34170
-56830
-59330
-71000
-104000
-126170
-137000
-106000
-82170
-65670
-34170
0
0
0
0
0
0
0
0
14500
17170
14000
-34330
-41830
-74170
-106500
-125000
-139500
-168500
-185830
-191670
-151670
-123330
-112330
-82500
-54000
-38170
0
0
0
0
0
0
0
0
0
-72670
-62330
-96000
-92000
-94500
-94830
-109000
-112500
-113330
-74670
-51330
-45330
0
0
0
0
0
0
0
0
0
16000
18420
11920
-42500
-46670
-75330
-104330
-105170
-102330
-122170
-134500
-138170
-108330
-79330
-65330
-36000
0
0
0
0
0
0
0
0
13670
17170
9670
-42170
-47670
-77500
-112000
-113170
-118170
-145670
-163330
-177670
-143330
-113170
-95500
-60000
-28170
0
0
0
0
0
0
0
0
0
0
-49500
-60830
-94330
-131830
-142000
-152170
-182000
-204330
-217330
-180670
-156830
-132170
-96670
-64000
-43330
-25170
0
0
0
0
0
0
0
0
-86330
-95500
-139500
-161170
-171170
-175830
-202170
-225670
-232670
-189670
-153670
-136670
-110000
-77330
-52000
-33830
-23500
0
0
0
0
0
0
0
-51830
-32000
-65170
-73330
-82500
-82170
-98670
-109830
-112670
-72670
-48500
-32670
-9830
-4330
-9170
1080
11000
30500
38330
44750
49920
53500
57080
50080
-12000
-37670
-33330
-21330
-16170
-26000
-35000
-29330
-38500
-10500
-830
-8000
-4830
-11330
2420
17500
22330
30080
33330
34830
36000
36830
37750
33670
-24830
-9000
-40330
-77330
-95830
-104500
-131000
-140830
-135000
-94500
-72670
-67330
-40170
-11830
-2500
-4330
-8500
-5830
-10330
-2830
1580
7920
14250
13420
-36000
-39500
-70330
-106000
-111670
-115830
-134670
-152000
-166500
-135000
-106000
-81830
-47000
-15830
-1830
-4500
-10500
-1670
3670
16750
25580
32080
37920
31830
-34000
-32000
-51000
-48670
-64830
-69170
-97830
-114170
-125000
-93330
-67830
-49000
-21170
-2830
-7170
-7670
-670
14420
23830
30170
37920
43830
48330
42080
-15670
-31000
-55830
-54670
-48830
-52330
-96500
-107170
-125000
-92830
-71000
-52670
-21830
-8330
-10170
-9500
-8830
4080
10330
21580
27250
32000
35830
30920
-23000
-10170
-42670
-53500
-82170
-88830
-117170
-129170
-125170
-86830
-63670
-55830
-30170
-7170
-1170
-3830
-8170
-3670
-11330
-4670
2920
9080
12500
9420
-47170
-53670
-81670
-118670
-122830
-128830
-152000
-170670
-179500
-140830
-115670
-94830
-56170
-24500
-10330
-3000
-5330
-4670
-7330
3920
14080
23420
28920
23920
-34500
-31830
-62170
-74500
-87170
-98670
-126670
-148670
-164000
-123830
-96830
-83170
-51330
-19830
-5170
-2170
-11500
-6670
-9000
-3830
-500
6170
13580
14170
-27330
-23500
-48500
-79500
-84170
-94330
-111670
-119670
-124000
-85830
-61830
-55170
-29670
-7000
-1830
-4500
-7500
-4000
-10170
-2830
1080
5420
9500
8420
-37330
-22830
-46330
-70000
-75670
-82330
-106000
-119670
-121170
-80670
-55500
-47170
-22000
-3330
-3500
-7500
-9000
670
3000
11830
17670
21170
24330
24500
-24330
-18670
-17330
-46670
-58000
-80000
-108830
-125670
-140000
-103830
-73670
-64000
-36330
-9500
-2670
-6170
-10830
-8000
-12000
-330
5420
13000
19580
18330
-31670
-40330
-63000
-89330
-93830
-100830
-122170
-135330
-139500
-100500
-69830
-52830
-22170
-1170
-2330
-8170
-8170
2750
8920
18250
23000
27170
30250
29420
-23170
-11000
-25670
-52330
-59330
-57330
-77000
-87000
-89830
-52830
-30670
-25500
-8330
-3000
-8170
-8170
-8170
4580
9500
14830
17250
19000
20420
18000
-26000
-12500
-36500
-58500
-73170
-86670
-104500
-113170
-124830
-90500
-64330
-54170
-27000
-5500
-3330
-7830
-8500
1830
5080
14420
21250
25420
28750
27670
-23500
-8830
-27830
-31830
-28500
-34330
-66330
-83500
-95670
-59000
-29330
-21330
-6000
-8500
-9830
5170
15420
30000
36330
42000
45920
50080
53830
49000
-12330
-30500
-38330
-31000
-46000
-41830
-76170
-72330
-105330
-65000
-34330
-23500
-4330
-8000
-12170
2080
10080
26500
33250
38170
42250
45750
48920
43170
-20500
-34000
-42000
-46670
-55830
-54170
-99330
-106000
-116330
-80830
-52330
-43830
-21330
-3330
-4670
-8000
-9670
-4170
-170
9330
15000
20330
23170
23420
-20170
-17000
-44830
-80500
-92830
-100330
-116170
-122830
-126330
-85670
-61830
-56500
-31670
-9330
-3830
-4670
-5500
-2670
-10670
-3500
-670
4170
10830
9500
-47000
-58830
-86330
-119330
-122830
-124500
-148000
-165670
-170670
-124830
-91670
-76500
-46170
-18000
-6330
-5830
-9670
-7000
-8500
2500
9000
17920
23580
21330
-33670
-43170
-53500
-80170
-82330
-91670
-114330
-129330
-137000
-96170
-59670
-47170
-19500
-1330
-4670
-11500
-5670
9000
17670
26670
31920
36420
40420
36000
-19830
-10830
-32830
-43330
-61170
-77170
-113170
-131500
-142170
-104170
-70170
-59170
-33000
-7830
-2000
-6670
-10170
-3830
1080
12500
19920
24670
28500
22920
-33830
-33500
-61170
-82170
-95330
-104330
-134000
-152830
-163000
-126670
-89330
-74830
-46500
-18330
-4670
-2000
-5500
-4670
-11500
-5170
-5670
250
4080
5500
-38000
-29830
-50670
-94670
-98170
-106830
-127670
-134330
-136170
-96500
-65000
-54500
-31500
-8500
-4500
-6500
-9170
0
1830
11170
19170
24000
28170
28330
-22830
-8500
-27170
-29500
-26500
-29170
-38830
-42670
-45330
-10830
-6830
-6000
-670
1170
12420
27080
31670
40750
43670
44420
44250
43580
43580
42080
5580
-36830
-38000
-51830
-67000
-81500
-109000
-118830
-123330
-80000
-45000
-33330
-10500
-5830
-10000
3170
13170
32750
41420
47420
52670
57170
60920
61080
4420
-15330
-35000
-39830
-30830
-39330
-53830
-54500
-64330
-34000
-16830
-10500
-3170
-8830
5170
23420
30170
41170
46000
49000
51750
54830
58330
53830
-5170
-27000
-38000
-37000
-25330
-23670
-34670
-28170
-37330
-9670
-2330
-6830
-1170
1500
15170
27170
32500
42500
46830
49670
52250
54670
56670
54170
4920
-6000
-18670
-12670
-4330
-13330
-35330
-37330
-64330
-27170
-12670
-11000
250
-3670
10920
28920
34830
44670
49080
52580
55420
57580
59750
58330
-4670
-26000
-34670
-35500
-30330
-39000
-51000
-40000
-43500
-15000
-4330
-9170
-4830
-8330
7330
23500
28750
37920
41330
43830
45670
46580
47830
47330
-10330
-27170
-36500
-40670
-42330
-45500
-80170
-70170
-76500
-39500
-15170
-12170
-4670
-7000
-500
14420
26330
38000
42920
47170
50920
53830
56170
56500
4250
3750
4830
3500
1500
3250
1080
4750
3580
6250
8830
14580
31830
46750
54580
61500
64170
71830
73830
75170
76330
77750
78170
75830
22750
580
-15830
-10000
-9500
-13670
-22330
-19830
-21000
1500
6580
15080
32420
48420
57170
64920
68500
76580
80830
83580
86330
89080
91080
91080
30830
27500
23670
19830
13500
18670
23330
8330
8330
22500
36670
41750
54250
69580
77420
84330
88000
96500
99250
101250
102920
104170
106250
99830
32500
20000
15670
14670
12580
14670
7000
5920
-5500
12250
23830
30330
48670
64500
73000
81170
85670
96420
100420
103170
106330
109500
111500
107830
36500
29920
22420
20080
12750
10750
7830
170
-8000
12670
27170
29330
42750
56500
63000
68750
70170
76330
77330
77580
77830
77580
77330
74920
22830
7670
5170
3170
1830
5000
-10500
-13000
250
6920
8420
14420
29420
42420
49170
55170
56670
63500
65420
67080
67830
68670
69170
68330
7330
4830
3750
3750
3080
4500
2170
5420
4500
6080
13500
21250
35170
49250
56170
62000
63250
69330
70250
70580
70000
69670
68920
66170
22580
-8500
-22670
-15330
-10670
-15330
-26000
-19670
-21500
-4170
-6330
1670
15750
33170
47170
56500
61500
71170
75330
78920
81580
84250
86330
85830
28580
23920
23920
19170
3420
6830
-14670
-20000
-20670
5920
12170
18920
37000
53500
64500
73330
77500
88250
92000
95330
98920
101670
104250
104420
33000
21330
11170
6420
1830
1250
-7830
-36830
-43000
-3170
9670
13830
28750
46750
57920
67080
71580
82170
87170
91420
95000
97580
101080
102580
33000
21500
15330
11670
6170
6000
830
-23830
-27500
3000
12670
16330
31920
47670
57250
66250
70920
80500
84830
88330
91250
94500
97670
98500
28170
17580
12750
5670
1250
250
-330
-24170
-28000
3330
11330
14250
29080
45500
54170
61250
63250
69330
69170
67920
66330
64420
62000
57750
21830
-19330
-24830
-18330
-10000
-17500
-32170
-34170
-44000
-10170
-5830
-8500
920
5920
18330
32920
37580
48000
54080
57500
60830
63920
66750
67420
7920
4750
4500
4330
2250
4500
-24830
-18500
-21000
4420
10500
17500
34670
49920
57830
65250
69080
77830
80750
82920
85170
87250
88670
87750
21830
12500
8420
2420
-12830
250
-28000
-25330
-24170
-2670
2170
7830
23830
37170
45080
51830
55000
61920
63420
64170
65000
66000
67170
65170
7250
3830
4000
1670
-6830
-13170
-27830
-21000
-22170
-2500
-8330
1000
13670
28920
40170
47830
51330
59500
62250
64420
65920
66920
69000
68500
80
-8330
-22000
-41500
-35670
-39670
-50670
-43330
-40000
-8500
-10000
-5830
4670
17580
32580
42920
48580
58500
62580
65580
68420
71170
73420
73580
23170
7750
-1500
-14000
-11830
-17830
-40670
-39670
-43830
-18670
-9170
-670
12250
26580
39080
50330
56580
66420
70500
75750
78500
82000
84580
86170
22420
15000
11420
4330
-7830
-670
-32330
-33670
-31500
2580
6580
12330
27330
43250
53750
62830
67580
77080
80830
83830
86580
88920
90920
90830
30000
26330
23250
19420
15670
18170
19000
330
-1000
17000
30670
33580
47250
61580
69080
76250
78920
86580
88830
90420
91830
92920
93830
92670
30080
27250
24750
21330
15830
19420
7920
7920
7330
22080
34000
36500
49670
63250
70420
76750
79000
85830
87830
89750
91080
92000
92750
91750
30750
27250
24000
20330
13580
18580
19420
750
170
18250
31750
34580
48500
62580
69670
76920
79170
86750
89080
90080
91920
93250
94420
93750
31330
25670
23170
12500
5170
3420
-19670
-18000
-20500
7500
16420
19920
34000
48250
55750
63000
65750
73080
74330
75330
76170
76500
76670
74420
23670
4420
-5170
-18670
-11500
-14830
-22670
-18500
-21500
2080
0
2670
12500
23500
31500
37580
39170
45250
46250
47250
47830
47420
49000
48580
1750
4750
-20170
170
-9000
-15670
-27000
-19500
-23330
1170
1250
5000
16580
32080
43920
51750
54670
63250
65750
67670
69420
71080
72250
71250
8080
6420
3920
3420
2750
5250
2000
4500
3830
5750
10080
15670
30420
44080
51170
58080
60580
68420
70750
72330
75000
77920
79750
79580
25750
7920
7830
6170
170
-11000
-19000
-14170
920
12420
22750
28500
43250
58330
66500
73920
76830
85170
87500
89330
91000
92170
93330
91920
30170
23580
22580
18000
3170
6000
-17330
-22170
-22170
7330
14500
20750
38170
54000
62920
71250
74830
82830
85670
88330
90000
92080
93420
92170
32830
27330
24750
21920
17500
21500
7330
7330
7080
23830
35080
36670
49330
61500
67750
73250
74580
80920
82920
83170
83500
83670
83330
81170
24920
22080
7170
5580
-8500
-12170
-23000
-25000
-23170
-170
-3330
2500
19670
34920
43670
51080
54830
64330
68080
71080
73670
76000
78000
78670
26080
7830
330
170
-4830
-10170
-21500
-21830
-20500
3170
10920
17830
31330
45170
52170
58580
60830
68500
71420
74080
75830
77750
80170
79920
26670
8830
7920
7170
8830
8170
7420
6000
4830
19580
31080
33080
45750
58420
64920
71080
73170
80330
82250
83920
84920
86580
88500
87670
29500
27500
11000
23920
19330
24250
24580
9670
10500
34670
48920
53250
68750
84250
92830
100920
104420
113000
116670
119500
121080
123170
125500
125670
52420
37580
32670
30670
27580
25170
19670
13170
12830
38420
53170
60330
79330
97420
108330
118420
123170
133330
137420
140080
142000
144080
146000
145330
70830
53170
48500
44250
42420
41170
34250
28920
25830
48920
61750
64580
76080
88750
94750
100080
101420
107170
109920
109330
109000
108920
109000
107170
46330
34420
27830
27080
26500
26830
24420
23170
22670
30580
41670
43080
55330
67170
74000
81080
82750
89750
91500
92580
93750
94920
95580
94250
30920
28500
26330
23420
19330
23330
23670
23830
9750
36250
50920
54830
70080
86170
94580
102670
106420
115170
118170
120420
122330
124170
125500
124920
60500
49670
38420
38830
38080
38250
29670
25670
24420
45000
59750
64000
78170
93080
101170
109330
113170
121500
124420
127420
129920
131250
133580
134420
59830
44920
38920
37330
34580
31500
24920
18750
18250
44750
58330
64500
83330
102080
113000
121750
126420
136080
139670
143500
145920
148330
150670
150500
86250
74920
64920
61000
58170
58080
48330
39080
36670
60330
75750
80670
95330
109670
117750
124420
127080
136330
139170
141250
142830
144250
145920
146330
78420
61830
53920
52500
51750
48670
38580
35330
32080
54670
68920
72420
86250
99830
107250
115000
118420
125920
127920
129580
130670
131330
131920
130420
67250
54000
46000
42830
37750
36330
26580
18330
17000
39500
53080
60920
76420
92080
101500
110080
114170
123420
127080
130330
133170
135750
137750
137250
74830
63830
52670
48250
44580
40670
31830
28170
25330
46250
60000
62830
77080
90830
97500
103330
104580
112750
118080
119500
121330
123080
125000
124920
62500
45080
32170
30000
27830
26420
18330
13580
20250
40670
57250
65920
84250
103830
117170
128330
135670
147670
155580
161080
166330
171170
175420
177500
113750
104000
97420
95500
94330
94920
86580
84330
82920
105170
118500
121500
133830
147580
154250
159920
160580
166420
166420
165330
163580
161000
158250
153250
99920
78250
65250
58920
55830
52580
40670
32250
27580
45670
54830
55580
67750
79920
86170
92670
94000
100830
102420
103330
104250
105170
105920
104330
41000
33000
27500
23750
21500
21500
22750
22750
7920
27250
39500
41330
53580
67080
73500
79170
80920
87830
89170
90000
90580
91000
91170
89670
28750
24580
22750
15170
3250
7250
0
0
0
6500
14830
21920
37920
53080
61170
68670
71500
79830
82750
84670
86670
90500
94000
94580
32920
27830
23580
19080
15330
18750
23250
23250
8420
31250
44500
47500
61580
76170
84000
91330
94750
103170
106000
108170
110170
111920
113420
112750
50080
43080
38250
39330
40000
41500
34500
31920
30750
51080
63000
65250
78330
91420
97920
103420
105500
113420
115330
116750
117670
118750
119670
118420
55000
46670
41500
42330
41500
42670
34920
32420
31750
54500
68170
71420
85750
100670
109830
118000
121750
130000
132670
134830
137250
139000
139920
141080
77580
61580
51000
50170
51250
53250
44580
43670
47000
75330
94420
104830
124920
145830
157830
167420
171830
181920
186670
190580
193580
195920
198000
197250
135000
120920
109250
101580
100750
94250
86670
82170
78750
99170
110250
112000
124920
138250
146080
151080
152920
160830
162330
162330
161830
161670
162170
160250
97420
84420
76330
76330
72750
71080
64420
60170
57420
77500
89420
89830
102420
113500
119080
122670
122580
128080
128250
127830
126750
125330
124250
121170
60080
47500
39920
37920
37080
36750
27830
26580
26420
42250
53670
54080
65580
77920
83920
89170
90500
97080
98080
98920
99080
99830
101580
101170
38330
32670
27670
22330
20420
24750
20080
15580
17920
36580
51750
62920
79500
97000
106750
115000
118750
127170
129080
130580
131420
131920
132250
131580
69330
59250
53830
54830
55670
57330
49420
46580
44580
67500
75420
76750
87750
98830
103330
107330
107250
112080
111500
110750
109750
108670
107670
105000
42170
20000
15000
9830
4750
4580
2500
0
0
9670
21580
27750
44250
59580
69170
77170
80670
88920
91830
93420
95000
97000
98420
97830
36330
29830
27920
25250
24830
26330
23670
23830
24330
34580
47830
51920
67170
83170
92420
101420
106170
116920
122330
126830
130920
135500
140170
142170
79420
60670
50500
54330
53920
54750
45500
43330
46250
72170
88420
96830
114500
132580
142920
152580
157750
168250
172920
177000
180500
183670
186420
186920
122000
104750
90580
87170
86420
85000
72580
65330
64420
89000
104830
112000
128920
145250
153920
162500
166750
176170
180080
183580
187250
189330
192000
192170
127330
112250
102500
96920
96670
94330
87330
84000
81750
104250
116330
117920
131000
144670
151330
157250
158170
164580
165000
164330
164080
163670
163000
160080
98750
84500
76750
75330
73080
70000
58250
55000
52670
73580
86330
88420
101750
115500
123330
130830
135170
144250
146750
150080
153000
155170
158330
158580
94080
74000
63250
64750
66670
59330
50420
46250
48750
71420
86170
89500
103750
118250
126250
132830
136420
145830
148420
150420
152250
153920
155250
155000
91750
82250
66420
57750
53250
49000
35000
32920
30580
48750
59670
64750
79920
95830
103580
111080
113920
122670
125580
128000
128830
133420
137670
137580
76330
61580
55420
54420
48580
46000
38420
35500
33580
57000
71580
75080
89080
103250
110580
117080
119000
126170
128250
129420
130000
130670
130830
129580
65420
57830
52670
52750
51920
50750
43000
41500
40420
62330
75080
78250
92500
104920
112000
119080
120670
127580
129000
129830
129830
129920
129830
127670
66500
54250
47000
42750
39830
39830
29670
25580
24920
45750
60500
64420
79250
92080
99670
106670
109500
117080
119250
122170
124330
126000
128000
128250
64830
56000
49420
49080
48750
45580
38920
38250
40250
64250
79330
83750
99250
114580
123250
131000
134080
142080
145420
148920
151420
154080
156580
156670
92330
81580
75250
73420
72500
69080
62000
60250
61750
86330
100920
104830
119920
134830
142500
149580
151920
159670
161920
163170
164580
165500
166250
164750
99750
89500
76750
69580
69670
69000
56330
51420
53330
78750
94830
103580
121580
138830
148750
158080
165670
175080
179080
183080
186830
187750
188920
188830
126830
107500
100000
101830
100170
97170
86000
83080
80750
101420
112670
113750
126080
138500
144580
149580
150580
156670
157420
157250
156670
156080
155250
152330
90330
77580
69330
66920
64830
63920
54000
49250
46170
66080
75920
75670
86580
96750
101580
105000
105250
112750
114170
115080
118170
122000
125750
127420
65250
59580
51000
48580
49250
48250
34830
25920
20250
32670
60000
66000
84250
106830
120000
132330
139420

## Test4
Test 4 | Sizing of 5x5 bore field based on an unbalanced ground load for a 20 year period with one peak duration (6 hours) | [21 empty] | Peak load duration of 6 hours
[23 empty] | Rb calculated by tool |  |  | Imposed Rb
Hourly Building Load |  | Month | Building monthly average load | Building monthly cooling peak load | Peak cooling hours | Building monthly heating peak load | Peak heating hours | Hourly Ground Load | Month | Ground monthly averaged load | Ground monthly cooling peak Load | Peak cooling hours | Ground monthly heating peak load | Peak heating hours |  | Ground yearly, monthly and hourly pulses | Parameter | Value | Units |  | Level | Sizing tool | Borehole length | Difference from mean | Rb calculated by tool | Borehole length | Difference from mean | Imposed Rb=0.2 m.k.W-1
(W) |  |  | (W) | (W) | (hr) | (W) | (hr) | (W) |  | (W) | (W) | (hr) | (W) | (hr) |  | (W) | Nb | 5×5 | ---- |  |  |  | (m) | % | (m.K/W) | m | % | (m.K/W)
qh |  |  | qm | qh,C | th,C | qh,H | th,H | qh |  | qm | qh,C | th,C | qh,H | th,H |  | Cooling | B | 8 | m | A | L2 | Classic ASHRAE sizing equation | 108.8 | -11.804 | 0.222 | 103.9 | -12.5138 | 0.2
0 |  | 1 | 10841.8414 | -28410 | 6 | 86380 | 6 | 0 | 1 | 7938.0475 | -35770.1036 | 6 | 64945.7568 | 6 | qh | -139731.2953 | D | 4 | m | B | L2 | Modified ASHRAE sizing equation | ---- | ----- | ----- | ---- | ----- | -----
0 |  | 2 | 6629.5833 | -42530 | 6 | 80780 | 6 | 0 | 2 | 3784.2277 | -53548.1347 | 6 | 60735.335 | 6 | qm | -46982.9784 | rb | 75 | mm | C | L2 | Modified + ASHRAE sizing equation -B | 131.2 | 6.3541 | 0.222 | 125.8 | 5.9265 | 0.2
3390 |  | 3 | -5822.6747 | -65990 | 6 | 57880 | 6 | 2548.8089 | 3 | -8085.1932 | -83085.8549 | 6 | 43517.7171 | 6 | qy | -19968.3733 | rp,o,rp,i | 16.7, 13 | mm | D | L2 | Modified + ASHRAE sizing equation- F | 130.4 | 5.7056 | 0.222 | 125.1 | 5.3371 | 0.2
6790 |  | 4 | -16559.0139 | -74300 | 6 | 50340 | 6 | 5105.1365 | 4 | -21107.3777 | -93548.7047 | 6 | 37848.6849 | 6 |  | Heating | 2dp | 83 | mm | E | L2 | Alternative method | 127.8 | 3.5979 | 0.222 | 122.5 | 3.1479 | 0.2
8790 |  | 5 | -27836.5591 | -95930 | 6 | 0 | 0 | 6608.8586 | 5 | -35048.103 | -120782.3316 | 6 | 0 | 0 | qh | 64945.7568 | mf | 0.074×139.731 | kg.s-1 | Est | L2 | Alternative method (short-term effects) | 123.5 | 0.11224 | 0.222 | 118.4 | -0.30442 | 0.2
10530 |  | 6 | -34680.9444 | -103960 | 6 | 0 | 0 | 7917.0968 | 6 | -43665.6451 | -130892.6425 | 6 | 0 | 0 | qm | 7938.0475 | ρf | 1026 | kg.m-3 | F | L2 | GHX design tool box | 98 | -20.5587 | 0.22 | 93 | -21.6918 | 0.2
55830 |  | 7 | -37315.6989 | -110980 | 6 | 0 | 0 | 41976.402 | 7 | -46982.9784 | -139731.2953 | 6 | 0 | 0 | qy | -19968.3733 | cp,f | 4019 | J.kg-1.K-1 | G | L3 | Modified Ashrae sizing equation -B (monthly) | 130.4 | 5.7056 | 0.222 | 125.1 | 5.3371 | 0.2
47190 |  | 8 | -35255.2285 | -104650 | 6 | 0 | 0 | 35480.3226 | 8 | -44388.7074 | -131761.399 | 6 | 0 | 0 |  |  | μf | 0.00337 | kg.s-1.m-1 | H | L3 | Alternative method (monthly) | 127 | 2.9494 | 0.22 | 121.7 | 2.4743 | 0.2
36230 |  | 9 | -27542.4583 | -88780 | 6 | 0 | 0 | 27239.9256 | 9 | -34677.8102 | -111780 | 6 | 0 | 0 |  |  | kf | 0.468 | W.m-1.K-1 | Hst | L3 | Alternative method (monthly,short-term effects) | 122.7 | -0.53626 | 0.22 | 117 | -1.4833 | 0.2
28410 |  | 10 | -14816.3038 | -77310 | 6 | 7630 | 6 | 21360.3722 | 10 | -18685.7431 | -97338.4974 | 6 | 5736.6998 | 6 |  |  | ρcp,g | 2052 | kJ.m-3.K-1 | I | L3 | EED monthly v.4.17 | 126 | 2.1388 | 0.211 | 123 | 3.5689 | 0.2
24320 |  | 11 | -1558.5 | -41970 | 6 | 56280 | 6 | 18285.2605 | 11 | -2982.9387 | -52843.057 | 6 | 42314.7395 | 6 |  |  | ρcp,gr | 3900 | kJ.m-3.K-1 | J | L3 | GLHEpro monthly v 5.0 | 123 | -0.29307 | 0.223 | 118.5 | -0.22022 | 0.2
21380 |  | 12 | 8324.9059 | -27230 | 6 | 76090 | 6 | 16074.7891 | 12 | 5852.6302 | -34284.4041 | 6 | 57209.1067 | 6 |  |  | ρcp,pipe | 1540 | kJ.m-3.K-1 | K | L4 | EED hourly v.4.17 | 123 | -0.29307 | 0.212 | 121 | 1.8848 | 0.2
19210 | [7 empty] | 14443.2506 | [8 empty] | αg | 0.08 | m2.day-1 | L | L4 | DST (COP:Cons.) | 131.9 | 6.9215 | 0.209 | 128.9 | 8.5368 | 0.2
16910 | [7 empty] | 12713.9702 | [8 empty] | kg | 1.9 | W.m-1.K-1 | X |  | Your tool
16280 | [7 empty] | 12240.2978 | [8 empty] | kgr | 0.69 | W.m-1.K-1
16800 | [7 empty] | 12631.2655 | [8 empty] | Tg | 15 | °C
19720 | [7 empty] | 14826.6998 | [8 empty] | kp | 0.4 | W.m-1.K-1
25630 | [7 empty] | 19270.1985 | [8 empty] | TL | 0 | °C
30970 | [7 empty] | 23285.1365 | [8 empty] | TH | 38 | °C |  |  | Mean | 123.3615 |  | 0.219 | 118.7615
36350 | [7 empty] | 27330.1489 | [8 empty] | Rb | 0.2 | m.K.W-1 |  |  | Min | 98 |  | 0.209 | 93
0 | [7 empty] | 0 | [8 empty] | t | 20 | years |  |  | Max | 131.9 |  | 0.223 | 128.9
1620 | [7 empty] | 1218.0149 | [8 empty] | Rc | 0 | m.K.W-1
8340 | [7 empty] | 6270.5211 | [8 empty] | hconv | 1000 | W.m-2.K-1
11860 | [7 empty] | 8917.072 | [8 empty] | q''g | 0 | W/m2
14290 | [7 empty] | 10744.0943 | [8 empty] | Fsc | 1.04 | -----
16330 | [7 empty] | 12277.8908 | [8 empty] | COPC | 3.86 | -----
18340 | [7 empty] | 13789.1315 | [8 empty] | COPH | 4.03 | -----
20430 | [7 empty] | 15360.5211
21820 | [7 empty] | 16405.6079
23050 | [7 empty] | 17330.397
72050 | [7 empty] | 54171.5881
66820 | [7 empty] | 50239.3548
54550 | [7 empty] | 41014.0199
41510 | [7 empty] | 31209.7519
29570 | [7 empty] | 22232.531
18800 | [7 empty] | 14134.9876
10530 | [7 empty] | 7917.0968
2990 | [7 empty] | 2248.0645
40 | [7 empty] | 30.0744
60 | [7 empty] | 45.1117
1990 | [7 empty] | 1496.2035
8840 | [7 empty] | 6646.4516
16220 | [7 empty] | 12195.1861
23860 | [7 empty] | 17939.4045
0 | [7 empty] | 0
0 | [7 empty] | 0
10 | [7 empty] | 7.5186
2090 | [7 empty] | 1571.3896
4550 | [7 empty] | 3420.9677
6930 | [7 empty] | 5210.397
8860 | [7 empty] | 6661.4888
10230 | [7 empty] | 7691.5385
11390 | [7 empty] | 8563.6973
11930 | [7 empty] | 8969.7022
55210 | [7 empty] | 41510.2481
43740 | [7 empty] | 32886.402
31890 | [7 empty] | 23976.8486
19970 | [7 empty] | 15014.665
10510 | [7 empty] | 7902.0596
1020 | [7 empty] | 766.8983
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-100 | [7 empty] | -125.9067
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
2790 | [7 empty] | 2097.6923
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
27260 | [7 empty] | 20495.732
22270 | [7 empty] | 16743.9454
13770 | [7 empty] | 10353.1266
7260 | [7 empty] | 5458.5112
2510 | [7 empty] | 1887.1712
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
1150 | [7 empty] | 864.6402
6850 | [7 empty] | 5150.2481
11450 | [7 empty] | 8608.8089
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
20 | [7 empty] | 15.0372
1170 | [7 empty] | 879.6774
3340 | [7 empty] | 2511.2159
5570 | [7 empty] | 4187.866
7150 | [7 empty] | 5375.8065
48120 | [7 empty] | 36179.5533
40590 | [7 empty] | 30518.0397
30160 | [7 empty] | 22676.129
18350 | [7 empty] | 13796.6501
6940 | [7 empty] | 5217.9156
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-70 | [7 empty] | -88.1347
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
1930 | [7 empty] | 1451.0918
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
27900 | [7 empty] | 20976.9231
22770 | [7 empty] | 17119.8759
18690 | [7 empty] | 14052.2829
14260 | [7 empty] | 10721.5385
10460 | [7 empty] | 7864.4665
10150 | [7 empty] | 7631.3896
8600 | [7 empty] | 6466.005
7980 | [7 empty] | 5999.8511
7330 | [7 empty] | 5511.1414
7810 | [7 empty] | 5872.0347
10100 | [7 empty] | 7593.7965
11790 | [7 empty] | 8864.4417
13020 | [7 empty] | 9789.2308
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
23360 | [7 empty] | 17563.4739
17890 | [7 empty] | 13450.794
14330 | [7 empty] | 10774.1687
11670 | [7 empty] | 8774.2184
10520 | [7 empty] | 7909.5782
10540 | [7 empty] | 7924.6154
12420 | [7 empty] | 9338.1141
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
310 | [7 empty] | 233.0769
930 | [7 empty] | 699.2308
1240 | [7 empty] | 932.3077
1490 | [7 empty] | 1120.273
1580 | [7 empty] | 1187.9404
39400 | [7 empty] | 29623.3251
26370 | [7 empty] | 19826.5757
15870 | [7 empty] | 11932.0347
9250 | [7 empty] | 6954.7146
5340 | [7 empty] | 4014.938
3190 | [7 empty] | 2398.4367
2010 | [7 empty] | 1511.2407
440 | [7 empty] | 330.8189
70 | [7 empty] | 52.6303
380 | [7 empty] | 285.7072
1840 | [7 empty] | 1383.4243
5910 | [7 empty] | 4443.4988
9870 | [7 empty] | 7420.8685
14310 | [7 empty] | 10759.1315
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
170 | [7 empty] | 127.8164
1020 | [7 empty] | 766.8983
2150 | [7 empty] | 1616.5012
2930 | [7 empty] | 2202.9529
42120 | [7 empty] | 31668.3871
32220 | [7 empty] | 24224.9628
22200 | [7 empty] | 16691.3151
14260 | [7 empty] | 10721.5385
10580 | [7 empty] | 7954.6898
5670 | [7 empty] | 4263.0521
960 | [7 empty] | 721.7866
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
1270 | [7 empty] | 954.8635
8200 | [7 empty] | 6165.2605
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
1700 | [7 empty] | 1278.1638
5130 | [7 empty] | 3857.0471
7710 | [7 empty] | 5796.8486
10170 | [7 empty] | 7646.4268
12310 | [7 empty] | 9255.4094
54400 | [7 empty] | 40901.2407
50280 | [7 empty] | 37803.5732
40270 | [7 empty] | 30277.4442
29810 | [7 empty] | 22412.9777
20440 | [7 empty] | 15368.0397
12630 | [7 empty] | 9496.005
6190 | [7 empty] | 4654.0199
1380 | [7 empty] | 1037.5682
210 | [7 empty] | 157.8908
1880 | [7 empty] | 1413.4988
5720 | [7 empty] | 4300.6452
13030 | [7 empty] | 9796.7494
19330 | [7 empty] | 14533.4739
26900 | [7 empty] | 20225.062
0 | [7 empty] | 0
0 | [7 empty] | 0
1820 | [7 empty] | 1368.3871
5760 | [7 empty] | 4330.7196
8120 | [7 empty] | 6105.1117
10500 | [7 empty] | 7894.5409
12550 | [7 empty] | 9435.8561
14730 | [7 empty] | 11074.9132
16820 | [7 empty] | 12646.3027
18370 | [7 empty] | 13811.6873
63950 | [7 empty] | 48081.5136
59500 | [7 empty] | 44735.732
46970 | [7 empty] | 35314.9132
33730 | [7 empty] | 25360.273
22470 | [7 empty] | 16894.3176
12330 | [7 empty] | 9270.4467
11150 | [7 empty] | 8383.2506
8400 | [7 empty] | 6315.6328
6690 | [7 empty] | 5029.9504
6480 | [7 empty] | 4872.0596
8280 | [7 empty] | 6225.4094
13620 | [7 empty] | 10240.3474
18300 | [7 empty] | 13759.0571
24710 | [7 empty] | 18578.4864
0 | [7 empty] | 0
0 | [7 empty] | 0
350 | [7 empty] | 263.1514
3850 | [7 empty] | 2894.665
6410 | [7 empty] | 4819.4293
8270 | [7 empty] | 6217.8908
9670 | [7 empty] | 7270.4963
10850 | [7 empty] | 8157.6923
11880 | [7 empty] | 8932.1092
12570 | [7 empty] | 9450.8933
56380 | [7 empty] | 42389.9256
47530 | [7 empty] | 35735.9553
37100 | [7 empty] | 27894.0447
29090 | [7 empty] | 21871.6377
23820 | [7 empty] | 17909.33
17720 | [7 empty] | 13322.9777
16340 | [7 empty] | 12285.4094
14200 | [7 empty] | 10676.4268
11070 | [7 empty] | 8323.1017
10450 | [7 empty] | 7856.9479
13100 | [7 empty] | 9849.3797
17550 | [7 empty] | 13195.1613
22390 | [7 empty] | 16834.1687
26860 | [7 empty] | 20194.9876
0 | [7 empty] | 0
0 | [7 empty] | 0
20 | [7 empty] | 15.0372
2670 | [7 empty] | 2007.469
6410 | [7 empty] | 4819.4293
9380 | [7 empty] | 7052.4566
11550 | [7 empty] | 8683.995
13510 | [7 empty] | 10157.6427
15280 | [7 empty] | 11488.4367
16860 | [7 empty] | 12676.3772
17740 | [7 empty] | 13338.0149
63200 | [7 empty] | 47517.6179
58740 | [7 empty] | 44164.3176
55100 | [7 empty] | 41427.5434
52730 | [7 empty] | 39645.6328
46740 | [7 empty] | 35141.9851
45580 | [7 empty] | 34269.8263
45660 | [7 empty] | 34329.9752
44470 | [7 empty] | 33435.2605
45020 | [7 empty] | 33848.7841
48090 | [7 empty] | 36156.9975
52810 | [7 empty] | 39705.7816
56060 | [7 empty] | 42149.33
58510 | [7 empty] | 43991.3896
1890 | [7 empty] | 1421.0174
17130 | [7 empty] | 12879.3797
20630 | [7 empty] | 15510.8933
22890 | [7 empty] | 17210.0993
24910 | [7 empty] | 18728.8586
26470 | [7 empty] | 19901.7618
27940 | [7 empty] | 21006.9975
29690 | [7 empty] | 22322.7543
30950 | [7 empty] | 23270.0993
31970 | [7 empty] | 24036.9975
33110 | [7 empty] | 24894.1191
34370 | [7 empty] | 25841.464
33160 | [7 empty] | 24931.7122
28480 | [7 empty] | 21413.0025
73720 | [7 empty] | 55427.196
62160 | [7 empty] | 46735.6824
51910 | [7 empty] | 39029.1067
45360 | [7 empty] | 34104.4169
41580 | [7 empty] | 31262.3821
40560 | [7 empty] | 30495.4839
42480 | [7 empty] | 31939.0571
0 | [7 empty] | 0
7660 | [7 empty] | 5759.2556
14520 | [7 empty] | 10917.0223
17580 | [7 empty] | 13217.7171
20220 | [7 empty] | 15202.6303
22470 | [7 empty] | 16894.3176
24360 | [7 empty] | 18315.335
26090 | [7 empty] | 19616.0546
28060 | [7 empty] | 21097.2208
29800 | [7 empty] | 22405.4591
31170 | [7 empty] | 23435.5087
32480 | [7 empty] | 24420.4467
33880 | [7 empty] | 25473.0521
86380 | [7 empty] | 64945.7568
80630 | [7 empty] | 60622.5558
66580 | [7 empty] | 50058.9082
51270 | [7 empty] | 38547.9156
37840 | [7 empty] | 28450.4218
25420 | [7 empty] | 19112.3077
15220 | [7 empty] | 11443.3251
7640 | [7 empty] | 5744.2184
3860 | [7 empty] | 2902.1836
3500 | [7 empty] | 2631.5136
6620 | [7 empty] | 4977.3201
15330 | [7 empty] | 11526.0298
23650 | [7 empty] | 17781.5136
31530 | [7 empty] | 23706.1787
0 | [7 empty] | 0
220 | [7 empty] | 165.4094
4520 | [7 empty] | 3398.4119
9010 | [7 empty] | 6774.268
12040 | [7 empty] | 9052.4069
14530 | [7 empty] | 10924.5409
16660 | [7 empty] | 12526.005
18170 | [7 empty] | 13661.3151
19370 | [7 empty] | 14563.5484
19920 | [7 empty] | 14977.072
67640 | [7 empty] | 50855.8809
59730 | [7 empty] | 44908.66
47030 | [7 empty] | 35360.0248
36100 | [7 empty] | 27142.1836
27620 | [7 empty] | 20766.402
21300 | [7 empty] | 16014.6402
16440 | [7 empty] | 12360.5955
13580 | [7 empty] | 10210.273
11370 | [7 empty] | 8548.66
11360 | [7 empty] | 8541.1414
13890 | [7 empty] | 10443.3499
20730 | [7 empty] | 15586.0794
27530 | [7 empty] | 20698.7345
33000 | [7 empty] | 24811.4144
0 | [7 empty] | 0
0 | [7 empty] | 0
3360 | [7 empty] | 2526.2531
6960 | [7 empty] | 5232.9529
8690 | [7 empty] | 6533.6725
10160 | [7 empty] | 7638.9082
11350 | [7 empty] | 8533.6228
12160 | [7 empty] | 9142.6303
12800 | [7 empty] | 9623.8213
13540 | [7 empty] | 10180.1985
59040 | [7 empty] | 44389.8759
48170 | [7 empty] | 36217.1464
37000 | [7 empty] | 27818.8586
29440 | [7 empty] | 22134.7891
24490 | [7 empty] | 18413.0769
20100 | [7 empty] | 15112.4069
16920 | [7 empty] | 12721.4888
12710 | [7 empty] | 9556.1538
11130 | [7 empty] | 8368.2134
11270 | [7 empty] | 8473.4739
13430 | [7 empty] | 10097.4938
18380 | [7 empty] | 13819.206
22930 | [7 empty] | 17240.1737
27230 | [7 empty] | 20473.1762
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
1640 | [7 empty] | 1233.0521
4280 | [7 empty] | 3217.9653
6130 | [7 empty] | 4608.9082
7260 | [7 empty] | 5458.5112
8300 | [7 empty] | 6240.4467
9210 | [7 empty] | 6924.6402
10230 | [7 empty] | 7691.5385
54310 | [7 empty] | 40833.5732
44120 | [7 empty] | 33172.1092
33380 | [7 empty] | 25097.1216
25050 | [7 empty] | 18834.1191
19290 | [7 empty] | 14503.3995
10560 | [7 empty] | 7939.6526
2000 | [7 empty] | 1503.7221
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
3680 | [7 empty] | 2766.8486
10510 | [7 empty] | 7902.0596
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
920 | [7 empty] | 691.7122
3350 | [7 empty] | 2518.7345
5520 | [7 empty] | 4150.273
7320 | [7 empty] | 5503.6228
8450 | [7 empty] | 6353.2258
49460 | [7 empty] | 37187.0471
41370 | [7 empty] | 31104.4913
30390 | [7 empty] | 22849.0571
19630 | [7 empty] | 14759.0323
12810 | [7 empty] | 9631.34
6170 | [7 empty] | 4638.9826
770 | [7 empty] | 578.933
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
2130 | [7 empty] | 1601.464
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
22010 | [7 empty] | 16548.4615
20130 | [7 empty] | 15134.9628
14590 | [7 empty] | 10969.6526
7050 | [7 empty] | 5300.6203
920 | [7 empty] | 691.7122
170 | [7 empty] | 127.8164
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
1870 | [7 empty] | 1405.9801
8720 | [7 empty] | 6556.2283
14430 | [7 empty] | 10849.3548
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
1250 | [7 empty] | 939.8263
3780 | [7 empty] | 2842.0347
6170 | [7 empty] | 4638.9826
8120 | [7 empty] | 6105.1117
10570 | [7 empty] | 7947.1712
12430 | [7 empty] | 9345.6328
13500 | [7 empty] | 10150.1241
14450 | [7 empty] | 10864.3921
12410 | [7 empty] | 9330.5955
6220 | [7 empty] | 4676.5757
42500 | [7 empty] | 31954.0943
22660 | [7 empty] | 17037.1712
11940 | [7 empty] | 8977.2208
5210 | [7 empty] | 3917.196
2070 | [7 empty] | 1556.3524
950 | [7 empty] | 714.268
760 | [7 empty] | 571.4144
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
800 | [7 empty] | 601.4888
2500 | [7 empty] | 1879.6526
4420 | [7 empty] | 3323.2258
6960 | [7 empty] | 5232.9529
50260 | [7 empty] | 37788.536
42750 | [7 empty] | 32142.0596
29920 | [7 empty] | 22495.6824
13180 | [7 empty] | 9909.5285
1360 | [7 empty] | 1022.531
0 | [7 empty] | 0
0 | [7 empty] | 0
-2570 | [7 empty] | -3235.8031
-8820 | [7 empty] | -11104.9741
-11570 | [7 empty] | -14567.4093
-9250 | [7 empty] | -11646.3731
-3110 | [7 empty] | -3915.6995
-200 | [7 empty] | -251.8135
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
12120 | [7 empty] | 9112.5558
9080 | [7 empty] | 6826.8983
2140 | [7 empty] | 1608.9826
0 | [7 empty] | 0
0 | [7 empty] | 0
-2290 | [7 empty] | -2883.2642
-16160 | [7 empty] | -20346.5285
-24140 | [7 empty] | -30393.886
-27910 | [7 empty] | -35140.5699
-28410 | [7 empty] | -35770.1036
-25190 | [7 empty] | -31715.9067
-15790 | [7 empty] | -19880.6736
-7130 | [7 empty] | -8977.1503
-1840 | [7 empty] | -2316.6839
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-230 | [7 empty] | -289.5855
530 | [7 empty] | 398.4864
0 | [7 empty] | 0
-890 | [7 empty] | -1120.5699
-1500 | [7 empty] | -1888.601
-2480 | [7 empty] | -3122.487
-3330 | [7 empty] | -4192.6943
-8040 | [7 empty] | -10122.9016
-11250 | [7 empty] | -14164.5078
-13000 | [7 empty] | -16367.8756
-12030 | [7 empty] | -15146.5803
-8260 | [7 empty] | -10399.8964
-4610 | [7 empty] | -5804.3005
-2060 | [7 empty] | -2593.6788
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-4460 | [7 empty] | -5615.4404
0 | [7 empty] | 0
0 | [7 empty] | 0
-660 | [7 empty] | -830.9845
-960 | [7 empty] | -1208.7047
-1130 | [7 empty] | -1422.7461
-1190 | [7 empty] | -1498.2902
-1590 | [7 empty] | -2001.9171
-1870 | [7 empty] | -2354.456
-2270 | [7 empty] | -2858.0829
-1930 | [7 empty] | -2430
-560 | [7 empty] | -705.0777
0 | [7 empty] | 0
2190 | [7 empty] | 1646.5757
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
100 | [7 empty] | 75.1861
880 | [7 empty] | 661.6377
1870 | [7 empty] | 1405.9801
3040 | [7 empty] | 2285.6576
37070 | [7 empty] | 27871.4888
31570 | [7 empty] | 23736.2531
21490 | [7 empty] | 16157.4938
9860 | [7 empty] | 7413.3499
1710 | [7 empty] | 1285.6824
0 | [7 empty] | 0
-230 | [7 empty] | -289.5855
-4980 | [7 empty] | -6270.1554
-11690 | [7 empty] | -14718.4974
-13690 | [7 empty] | -17236.6321
-10920 | [7 empty] | -13749.0155
-2550 | [7 empty] | -3210.6218
-280 | [7 empty] | -352.5389
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
25540 | [7 empty] | 19202.531
22100 | [7 empty] | 16616.129
18100 | [7 empty] | 13608.6849
11640 | [7 empty] | 8751.6625
6500 | [7 empty] | 4887.0968
2210 | [7 empty] | 1661.6129
360 | [7 empty] | 270.67
0 | [7 empty] | 0
0 | [7 empty] | 0
700 | [7 empty] | 526.3027
4720 | [7 empty] | 3548.7841
8560 | [7 empty] | 6435.9305
12130 | [7 empty] | 9120.0744
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
650 | [7 empty] | 488.7097
2290 | [7 empty] | 1721.7618
3820 | [7 empty] | 2872.1092
4970 | [7 empty] | 3736.7494
6040 | [7 empty] | 4541.2407
7420 | [7 empty] | 5578.8089
8640 | [7 empty] | 6496.0794
8000 | [7 empty] | 6014.8883
4700 | [7 empty] | 3533.7469
41280 | [7 empty] | 31036.8238
28090 | [7 empty] | 21119.7767
20640 | [7 empty] | 15518.4119
15640 | [7 empty] | 11759.1067
13290 | [7 empty] | 9992.2333
14390 | [7 empty] | 10819.2804
18380 | [7 empty] | 13819.206
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
2620 | [7 empty] | 1969.8759
6830 | [7 empty] | 5135.2109
9960 | [7 empty] | 7488.536
12340 | [7 empty] | 9277.9653
14430 | [7 empty] | 10849.3548
16340 | [7 empty] | 12285.4094
17690 | [7 empty] | 13300.4218
18640 | [7 empty] | 14014.6898
19780 | [7 empty] | 14871.8114
21100 | [7 empty] | 15864.268
69280 | [7 empty] | 52088.933
61630 | [7 empty] | 46337.196
48240 | [7 empty] | 36269.7767
34120 | [7 empty] | 25653.4988
21710 | [7 empty] | 16322.9032
12990 | [7 empty] | 9766.6749
5880 | [7 empty] | 4420.9429
580 | [7 empty] | 436.0794
0 | [7 empty] | 0
0 | [7 empty] | 0
180 | [7 empty] | 135.335
5050 | [7 empty] | 3796.8983
11590 | [7 empty] | 8714.0695
19420 | [7 empty] | 14601.1414
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
550 | [7 empty] | 413.5236
4220 | [7 empty] | 3172.8536
6900 | [7 empty] | 5187.8412
9570 | [7 empty] | 7195.3102
11500 | [7 empty] | 8646.402
12750 | [7 empty] | 9586.2283
14370 | [7 empty] | 10804.2432
58580 | [7 empty] | 44044.0199
52060 | [7 empty] | 39141.8859
40570 | [7 empty] | 30503.0025
25120 | [7 empty] | 18886.7494
11150 | [7 empty] | 8383.2506
1200 | [7 empty] | 902.2333
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
40 | [7 empty] | 30.0744
4920 | [7 empty] | 3699.1563
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
280 | [7 empty] | 210.5211
36260 | [7 empty] | 27262.4814
27430 | [7 empty] | 20623.5484
18050 | [7 empty] | 13571.0918
9930 | [7 empty] | 7465.9801
4410 | [7 empty] | 3315.7072
1480 | [7 empty] | 1112.7543
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
1990 | [7 empty] | 1496.2035
7080 | [7 empty] | 5323.1762
11770 | [7 empty] | 8849.4045
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
70 | [7 empty] | 52.6303
2410 | [7 empty] | 1811.9851
6510 | [7 empty] | 4894.6154
10200 | [7 empty] | 7668.9826
13460 | [7 empty] | 10120.0496
16570 | [7 empty] | 12458.3375
60530 | [7 empty] | 45510.1489
60440 | [7 empty] | 45442.4814
49150 | [7 empty] | 36953.9702
37700 | [7 empty] | 28345.1613
28230 | [7 empty] | 21225.0372
19570 | [7 empty] | 14713.9206
12940 | [7 empty] | 9729.0819
7180 | [7 empty] | 5398.3623
4340 | [7 empty] | 3263.0769
4820 | [7 empty] | 3623.9702
8850 | [7 empty] | 6653.9702
17600 | [7 empty] | 13232.7543
25550 | [7 empty] | 19210.0496
32170 | [7 empty] | 24187.3697
0 | [7 empty] | 0
230 | [7 empty] | 172.928
5620 | [7 empty] | 4225.4591
9740 | [7 empty] | 7323.1266
12670 | [7 empty] | 9526.0794
14860 | [7 empty] | 11172.6551
16710 | [7 empty] | 12563.598
18270 | [7 empty] | 13736.5012
19360 | [7 empty] | 14556.0298
20600 | [7 empty] | 15488.3375
67380 | [7 empty] | 50660.397
62030 | [7 empty] | 46637.9404
49500 | [7 empty] | 37217.1216
36690 | [7 empty] | 27585.7816
25610 | [7 empty] | 19255.1613
14990 | [7 empty] | 11270.397
6940 | [7 empty] | 5217.9156
4010 | [7 empty] | 3014.9628
4370 | [7 empty] | 3285.6328
3740 | [7 empty] | 2811.9603
5830 | [7 empty] | 4383.3499
11220 | [7 empty] | 8435.8809
16970 | [7 empty] | 12759.0819
22420 | [7 empty] | 16856.7246
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
1230 | [7 empty] | 924.7891
3800 | [7 empty] | 2857.072
5540 | [7 empty] | 4165.3102
6950 | [7 empty] | 5225.4342
8040 | [7 empty] | 6044.9628
9090 | [7 empty] | 6834.4169
9880 | [7 empty] | 7428.3871
53050 | [7 empty] | 39886.2283
45080 | [7 empty] | 33893.8958
39350 | [7 empty] | 29585.732
36480 | [7 empty] | 27427.8908
33500 | [7 empty] | 25187.3449
29640 | [7 empty] | 22285.1613
27730 | [7 empty] | 20849.1067
26900 | [7 empty] | 20225.062
27220 | [7 empty] | 20465.6576
29080 | [7 empty] | 21864.1191
33680 | [7 empty] | 25322.6799
36570 | [7 empty] | 27495.5583
39130 | [7 empty] | 29420.3226
0 | [7 empty] | 0
1210 | [7 empty] | 909.7519
6780 | [7 empty] | 5097.6179
9460 | [7 empty] | 7112.6055
11150 | [7 empty] | 8383.2506
12700 | [7 empty] | 9548.6352
14020 | [7 empty] | 10541.0918
15040 | [7 empty] | 11307.9901
15920 | [7 empty] | 11969.6278
16660 | [7 empty] | 12526.005
17100 | [7 empty] | 12856.8238
17290 | [7 empty] | 12999.6774
16190 | [7 empty] | 12172.6303
13880 | [7 empty] | 10435.8313
60390 | [7 empty] | 45404.8883
51120 | [7 empty] | 38435.1365
45200 | [7 empty] | 33984.1191
43790 | [7 empty] | 32923.995
42700 | [7 empty] | 32104.4665
41990 | [7 empty] | 31570.6452
42050 | [7 empty] | 31615.7568
0 | [7 empty] | 0
2210 | [7 empty] | 1661.6129
7650 | [7 empty] | 5751.737
9410 | [7 empty] | 7075.0124
10520 | [7 empty] | 7909.5782
11430 | [7 empty] | 8593.7717
12000 | [7 empty] | 9022.3325
12400 | [7 empty] | 9323.0769
12720 | [7 empty] | 9563.6725
12720 | [7 empty] | 9563.6725
11730 | [7 empty] | 8819.33
10480 | [7 empty] | 7879.5037
10070 | [7 empty] | 7571.2407
57610 | [7 empty] | 43314.7146
40000 | [7 empty] | 30074.4417
28170 | [7 empty] | 21179.9256
16540 | [7 empty] | 12435.7816
6180 | [7 empty] | 4646.5012
160 | [7 empty] | 120.2978
0 | [7 empty] | 0
0 | [7 empty] | 0
-890 | [7 empty] | -1120.5699
-3100 | [7 empty] | -3903.1088
-2750 | [7 empty] | -3462.4352
0 | [7 empty] | 0
0 | [7 empty] | 0
1660 | [7 empty] | 1248.0893
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
360 | [7 empty] | 270.67
2420 | [7 empty] | 1819.5037
42310 | [7 empty] | 31811.2407
37430 | [7 empty] | 28142.1588
24070 | [7 empty] | 18097.2953
8500 | [7 empty] | 6390.8189
0 | [7 empty] | 0
0 | [7 empty] | 0
-210 | [7 empty] | -264.4041
-8790 | [7 empty] | -11067.2021
-14550 | [7 empty] | -18319.4301
-17550 | [7 empty] | -22096.6321
-15200 | [7 empty] | -19137.8238
-5770 | [7 empty] | -7264.8187
-850 | [7 empty] | -1070.2073
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
17280 | [7 empty] | 12992.1588
13860 | [7 empty] | 10420.794
8330 | [7 empty] | 6263.0025
3400 | [7 empty] | 2556.3275
1030 | [7 empty] | 774.4169
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
390 | [7 empty] | 293.2258
5640 | [7 empty] | 4240.4963
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
26050 | [7 empty] | 19585.9801
19510 | [7 empty] | 14668.8089
11850 | [7 empty] | 8909.5533
3120 | [7 empty] | 2345.8065
690 | [7 empty] | 518.7841
290 | [7 empty] | 218.0397
2290 | [7 empty] | 1721.7618
3790 | [7 empty] | 2849.5533
5190 | [7 empty] | 3902.1588
7580 | [7 empty] | 5699.1067
11570 | [7 empty] | 8699.0323
18650 | [7 empty] | 14022.2084
24350 | [7 empty] | 18307.8164
30490 | [7 empty] | 22924.2432
0 | [7 empty] | 0
240 | [7 empty] | 180.4467
3880 | [7 empty] | 2917.2208
7810 | [7 empty] | 5872.0347
11370 | [7 empty] | 8548.66
14090 | [7 empty] | 10593.7221
16150 | [7 empty] | 12142.5558
18130 | [7 empty] | 13631.2407
19890 | [7 empty] | 14954.5161
21870 | [7 empty] | 16443.201
67860 | [7 empty] | 51021.2903
66940 | [7 empty] | 50329.5782
54840 | [7 empty] | 41232.0596
42870 | [7 empty] | 32232.2829
32800 | [7 empty] | 24661.0422
24400 | [7 empty] | 18345.4094
17800 | [7 empty] | 13383.1266
11830 | [7 empty] | 8894.5161
9450 | [7 empty] | 7105.0868
10010 | [7 empty] | 7526.129
14660 | [7 empty] | 11022.2829
23900 | [7 empty] | 17969.4789
33460 | [7 empty] | 25157.2705
41320 | [7 empty] | 31066.8983
0 | [7 empty] | 0
6830 | [7 empty] | 5135.2109
14150 | [7 empty] | 10638.8337
17770 | [7 empty] | 13360.5707
20380 | [7 empty] | 15322.928
22740 | [7 empty] | 17097.3201
24920 | [7 empty] | 18736.3772
27020 | [7 empty] | 20315.2854
28720 | [7 empty] | 21593.4491
30730 | [7 empty] | 23104.6898
32320 | [7 empty] | 24300.1489
80780 | [7 empty] | 60735.335
76670 | [7 empty] | 57645.1861
64530 | [7 empty] | 48517.5931
52350 | [7 empty] | 39359.9256
41450 | [7 empty] | 31164.6402
32750 | [7 empty] | 24623.4491
25320 | [7 empty] | 19037.1216
20330 | [7 empty] | 15285.335
18780 | [7 empty] | 14119.9504
20490 | [7 empty] | 15405.6328
25820 | [7 empty] | 19413.0521
32340 | [7 empty] | 24315.1861
36820 | [7 empty] | 27683.5236
0 | [7 empty] | 0
1150 | [7 empty] | 864.6402
7770 | [7 empty] | 5841.9603
11090 | [7 empty] | 8338.139
13710 | [7 empty] | 10308.0149
16070 | [7 empty] | 12082.4069
18080 | [7 empty] | 13593.6476
19590 | [7 empty] | 14728.9578
21080 | [7 empty] | 15849.2308
22570 | [7 empty] | 16969.5037
23830 | [7 empty] | 17916.8486
24700 | [7 empty] | 18570.9677
21860 | [7 empty] | 16435.6824
14630 | [7 empty] | 10999.727
55570 | [7 empty] | 41780.9181
36620 | [7 empty] | 27533.1514
25110 | [7 empty] | 18879.2308
16340 | [7 empty] | 12285.4094
10570 | [7 empty] | 7947.1712
8680 | [7 empty] | 6526.1538
10480 | [7 empty] | 7879.5037
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
470 | [7 empty] | 353.3747
3970 | [7 empty] | 2984.8883
7340 | [7 empty] | 5518.66
9220 | [7 empty] | 6932.1588
10500 | [7 empty] | 7894.5409
11890 | [7 empty] | 8939.6278
13530 | [7 empty] | 10172.6799
14890 | [7 empty] | 11195.2109
15790 | [7 empty] | 11871.8859
62810 | [7 empty] | 47224.3921
50850 | [7 empty] | 38232.134
38240 | [7 empty] | 28751.1663
27150 | [7 empty] | 20413.0273
20570 | [7 empty] | 15465.7816
10990 | [7 empty] | 8262.9529
4480 | [7 empty] | 3368.3375
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
2950 | [7 empty] | 2217.9901
7050 | [7 empty] | 5300.6203
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
1560 | [7 empty] | 1172.9032
4960 | [7 empty] | 3729.2308
7720 | [7 empty] | 5804.3672
48650 | [7 empty] | 36578.0397
44730 | [7 empty] | 33630.7444
35620 | [7 empty] | 26781.2903
28600 | [7 empty] | 21503.2258
24020 | [7 empty] | 18059.7022
20380 | [7 empty] | 15322.928
18210 | [7 empty] | 13691.3896
16430 | [7 empty] | 12353.0769
16510 | [7 empty] | 12413.2258
17230 | [7 empty] | 12954.5658
21090 | [7 empty] | 15856.7494
27540 | [7 empty] | 20706.2531
34740 | [7 empty] | 26119.6526
40740 | [7 empty] | 30630.8189
0 | [7 empty] | 0
3170 | [7 empty] | 2383.3995
9730 | [7 empty] | 7315.6079
13690 | [7 empty] | 10292.9777
16690 | [7 empty] | 12548.5608
19280 | [7 empty] | 14495.8809
21730 | [7 empty] | 16337.9404
24060 | [7 empty] | 18089.7767
26090 | [7 empty] | 19616.0546
27570 | [7 empty] | 20728.8089
76940 | [7 empty] | 57848.1886
73050 | [7 empty] | 54923.4491
58920 | [7 empty] | 44299.6526
44950 | [7 empty] | 33796.1538
33190 | [7 empty] | 24954.268
22450 | [7 empty] | 16879.2804
13640 | [7 empty] | 10255.3846
5740 | [7 empty] | 4315.6824
1160 | [7 empty] | 872.1588
740 | [7 empty] | 556.3772
2690 | [7 empty] | 2022.5062
9330 | [7 empty] | 7014.8635
18110 | [7 empty] | 13616.2035
26630 | [7 empty] | 20022.0596
0 | [7 empty] | 0
0 | [7 empty] | 0
2890 | [7 empty] | 2172.8784
7790 | [7 empty] | 5856.9975
10230 | [7 empty] | 7691.5385
11850 | [7 empty] | 8909.5533
13660 | [7 empty] | 10270.4218
15400 | [7 empty] | 11578.66
16240 | [7 empty] | 12210.2233
17070 | [7 empty] | 12834.268
63510 | [7 empty] | 47750.6948
54630 | [7 empty] | 41074.1687
41560 | [7 empty] | 31247.3449
25720 | [7 empty] | 19337.866
16030 | [7 empty] | 12052.3325
5080 | [7 empty] | 3819.4541
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
1360 | [7 empty] | 1022.531
5370 | [7 empty] | 4037.4938
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
60 | [7 empty] | 45.1117
35790 | [7 empty] | 26909.1067
28720 | [7 empty] | 21593.4491
17040 | [7 empty] | 12811.7122
3940 | [7 empty] | 2962.3325
0 | [7 empty] | 0
0 | [7 empty] | 0
-1160 | [7 empty] | -1460.5181
-10210 | [7 empty] | -12855.0777
-12850 | [7 empty] | -16179.0155
-16870 | [7 empty] | -21240.4663
-14510 | [7 empty] | -18269.0674
-7870 | [7 empty] | -9908.8601
-3030 | [7 empty] | -3814.9741
-310 | [7 empty] | -390.3109
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
10110 | [7 empty] | 7601.3151
7440 | [7 empty] | 5593.8462
40 | [7 empty] | 30.0744
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-940 | [7 empty] | -1183.5233
-3770 | [7 empty] | -4746.6839
-4860 | [7 empty] | -6119.0674
-3440 | [7 empty] | -4331.1917
-1270 | [7 empty] | -1599.0155
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-1110 | [7 empty] | -1397.5648
-9410 | [7 empty] | -11847.8238
-12820 | [7 empty] | -16141.2435
-11300 | [7 empty] | -14227.4611
-10830 | [7 empty] | -13635.6995
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
5470 | [7 empty] | 4112.6799
5290 | [7 empty] | 3977.3449
390 | [7 empty] | 293.2258
0 | [7 empty] | 0
-1340 | [7 empty] | -1687.1503
-4300 | [7 empty] | -5413.9896
-13840 | [7 empty] | -17425.4922
-22490 | [7 empty] | -28316.4249
-30730 | [7 empty] | -38691.1399
-29620 | [7 empty] | -37293.5751
-26780 | [7 empty] | -33717.8238
-19390 | [7 empty] | -24413.3161
-10970 | [7 empty] | -13811.9689
-4380 | [7 empty] | -5514.715
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-4390 | [7 empty] | -5527.3057
-190 | [7 empty] | -239.2228
-1450 | [7 empty] | -1825.6477
-3480 | [7 empty] | -4381.5544
-9890 | [7 empty] | -12452.1762
-18830 | [7 empty] | -23708.2383
-24460 | [7 empty] | -30796.7876
-31160 | [7 empty] | -39232.5389
-39740 | [7 empty] | -50035.3368
-42530 | [7 empty] | -53548.1347
-38570 | [7 empty] | -48562.228
-29790 | [7 empty] | -37507.6166
-19790 | [7 empty] | -24916.943
-11520 | [7 empty] | -14504.456
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-7250 | [7 empty] | -9128.2383
-2080 | [7 empty] | -2618.8601
-4620 | [7 empty] | -5816.8912
-11680 | [7 empty] | -14705.9067
-15650 | [7 empty] | -19704.4041
-18410 | [7 empty] | -23179.4301
-20320 | [7 empty] | -25584.2487
-26350 | [7 empty] | -33176.4249
-28130 | [7 empty] | -35417.5648
-28370 | [7 empty] | -35719.7409
-24540 | [7 empty] | -30897.513
-17460 | [7 empty] | -21983.3161
-9470 | [7 empty] | -11923.3679
-3120 | [7 empty] | -3928.2902
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-7270 | [7 empty] | -9153.4197
-3590 | [7 empty] | -4520.0518
-6840 | [7 empty] | -8612.0207
-14110 | [7 empty] | -17765.4404
-18480 | [7 empty] | -23267.5648
-24940 | [7 empty] | -31401.1399
-31310 | [7 empty] | -39421.399
-35750 | [7 empty] | -45011.658
-37860 | [7 empty] | -47668.2902
-35710 | [7 empty] | -44961.2953
-31270 | [7 empty] | -39371.0363
-21940 | [7 empty] | -27623.9378
-11600 | [7 empty] | -14605.1813
-3560 | [7 empty] | -4482.2798
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
9090 | [7 empty] | 6834.4169
13040 | [7 empty] | 9804.268
5140 | [7 empty] | 3864.5658
70 | [7 empty] | 52.6303
-920 | [7 empty] | -1158.342
-2410 | [7 empty] | -3034.3523
-7310 | [7 empty] | -9203.7824
-15150 | [7 empty] | -19074.8705
-18260 | [7 empty] | -22990.5699
-17850 | [7 empty] | -22474.3523
-14720 | [7 empty] | -18533.4715
-5320 | [7 empty] | -6698.2383
-820 | [7 empty] | -1032.4352
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
260 | [7 empty] | 195.4839
1680 | [7 empty] | 1263.1266
3230 | [7 empty] | 2428.5112
35390 | [7 empty] | 26608.3623
28310 | [7 empty] | 21285.1861
16870 | [7 empty] | 12683.8958
6440 | [7 empty] | 4841.9851
1070 | [7 empty] | 804.4913
0 | [7 empty] | 0
0 | [7 empty] | 0
-220 | [7 empty] | -276.9948
-60 | [7 empty] | -75.544
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
320 | [7 empty] | 240.5955
1550 | [7 empty] | 1165.3846
2290 | [7 empty] | 1721.7618
2380 | [7 empty] | 1789.4293
850 | [7 empty] | 639.0819
0 | [7 empty] | 0
14990 | [7 empty] | 11270.397
1670 | [7 empty] | 1255.6079
190 | [7 empty] | 142.8536
-30 | [7 empty] | -37.772
-2020 | [7 empty] | -2543.3161
-3820 | [7 empty] | -4809.6373
-3390 | [7 empty] | -4268.2383
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
12810 | [7 empty] | 9631.34
8790 | [7 empty] | 6608.8586
3180 | [7 empty] | 2390.9181
350 | [7 empty] | 263.1514
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-120 | [7 empty] | -151.0881
-500 | [7 empty] | -629.5337
-680 | [7 empty] | -856.1658
-610 | [7 empty] | -768.0311
-160 | [7 empty] | -201.4508
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-400 | [7 empty] | -503.6269
0 | [7 empty] | 0
-230 | [7 empty] | -289.5855
-1570 | [7 empty] | -1976.7358
-11850 | [7 empty] | -14919.9482
-22370 | [7 empty] | -28165.3368
-29680 | [7 empty] | -37369.1192
-35540 | [7 empty] | -44747.2539
-38280 | [7 empty] | -48197.0984
-38060 | [7 empty] | -47920.1036
-33770 | [7 empty] | -42518.7047
-25030 | [7 empty] | -31514.456
-12480 | [7 empty] | -15713.1606
-3430 | [7 empty] | -4318.601
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
6860 | [7 empty] | 5157.7667
6740 | [7 empty] | 5067.5434
340 | [7 empty] | 255.6328
-900 | [7 empty] | -1133.1606
-2010 | [7 empty] | -2530.7254
-6350 | [7 empty] | -7995.0777
-13820 | [7 empty] | -17400.3109
-16100 | [7 empty] | -20270.9845
-15350 | [7 empty] | -19326.6839
-18010 | [7 empty] | -22675.8031
-16940 | [7 empty] | -21328.601
-11440 | [7 empty] | -14403.7306
-3700 | [7 empty] | -4658.5492
-1070 | [7 empty] | -1347.2021
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
3040 | [7 empty] | 2285.6576
4580 | [7 empty] | 3443.5236
0 | [7 empty] | 0
-800 | [7 empty] | -1007.2539
-1710 | [7 empty] | -2153.0052
-11470 | [7 empty] | -14441.5026
-17920 | [7 empty] | -22562.487
-20120 | [7 empty] | -25332.4352
-20620 | [7 empty] | -25961.9689
-21000 | [7 empty] | -26440.4145
-16390 | [7 empty] | -20636.114
-8230 | [7 empty] | -10362.1244
-1990 | [7 empty] | -2505.544
-160 | [7 empty] | -201.4508
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
10010 | [7 empty] | 7526.129
10470 | [7 empty] | 7871.9851
2630 | [7 empty] | 1977.3945
0 | [7 empty] | 0
-700 | [7 empty] | -881.3472
-3600 | [7 empty] | -4532.6425
-12230 | [7 empty] | -15398.3938
-20760 | [7 empty] | -26138.2383
-26170 | [7 empty] | -32949.7927
-27840 | [7 empty] | -35052.4352
-24580 | [7 empty] | -30947.8756
-16510 | [7 empty] | -20787.2021
-5410 | [7 empty] | -6811.5544
-1010 | [7 empty] | -1271.658
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
17270 | [7 empty] | 12984.6402
10200 | [7 empty] | 7668.9826
2160 | [7 empty] | 1624.0199
0 | [7 empty] | 0
0 | [7 empty] | 0
-5720 | [7 empty] | -7201.8653
-14110 | [7 empty] | -17765.4404
-17970 | [7 empty] | -22625.4404
-18060 | [7 empty] | -22738.7565
-15030 | [7 empty] | -18923.7824
-8860 | [7 empty] | -11155.3368
-2520 | [7 empty] | -3172.8497
-310 | [7 empty] | -390.3109
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
3160 | [7 empty] | 2375.8809
0 | [7 empty] | 0
0 | [7 empty] | 0
-1830 | [7 empty] | -2304.0933
-6300 | [7 empty] | -7932.1244
-7230 | [7 empty] | -9103.057
-4440 | [7 empty] | -5590.2591
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
19290 | [7 empty] | 14503.3995
16140 | [7 empty] | 12135.0372
6570 | [7 empty] | 4939.727
640 | [7 empty] | 481.1911
0 | [7 empty] | 0
0 | [7 empty] | 0
-4810 | [7 empty] | -6056.114
-13570 | [7 empty] | -17085.544
-21420 | [7 empty] | -26969.2228
-20840 | [7 empty] | -26238.9637
-18690 | [7 empty] | -23531.9689
-11230 | [7 empty] | -14139.3264
-2780 | [7 empty] | -3500.2073
-130 | [7 empty] | -163.6788
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
18680 | [7 empty] | 14044.7643
15350 | [7 empty] | 11541.067
5520 | [7 empty] | 4150.273
0 | [7 empty] | 0
0 | [7 empty] | 0
-3190 | [7 empty] | -4016.4249
-13350 | [7 empty] | -16808.5492
-21890 | [7 empty] | -27560.9845
-27050 | [7 empty] | -34057.772
-27160 | [7 empty] | -34196.2694
-23060 | [7 empty] | -29034.0933
-16370 | [7 empty] | -20610.9326
-6390 | [7 empty] | -8045.4404
-1380 | [7 empty] | -1737.513
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
6060 | [7 empty] | 4556.2779
7220 | [7 empty] | 5428.4367
340 | [7 empty] | 255.6328
-260 | [7 empty] | -327.3575
-1430 | [7 empty] | -1800.4663
-6480 | [7 empty] | -8158.7565
-14260 | [7 empty] | -17954.3005
-20620 | [7 empty] | -25961.9689
-21700 | [7 empty] | -27321.7617
-23010 | [7 empty] | -28971.1399
-20140 | [7 empty] | -25357.6166
-13960 | [7 empty] | -17576.5803
-7510 | [7 empty] | -9455.5959
-3180 | [7 empty] | -4003.8342
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-2940 | [7 empty] | -3701.658
0 | [7 empty] | 0
-920 | [7 empty] | -1158.342
-1760 | [7 empty] | -2215.9585
-3050 | [7 empty] | -3840.1554
-5020 | [7 empty] | -6320.5181
-7600 | [7 empty] | -9568.9119
-11110 | [7 empty] | -13988.2383
-13080 | [7 empty] | -16468.601
-13850 | [7 empty] | -17438.0829
-12080 | [7 empty] | -15209.5337
-8750 | [7 empty] | -11016.8394
-3020 | [7 empty] | -3802.3834
-1370 | [7 empty] | -1724.9223
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-2540 | [7 empty] | -3198.0311
80 | [7 empty] | 60.1489
-830 | [7 empty] | -1045.0259
-1770 | [7 empty] | -2228.5492
-3520 | [7 empty] | -4431.9171
-8270 | [7 empty] | -10412.487
-12580 | [7 empty] | -15839.0674
-16930 | [7 empty] | -21316.0104
-19750 | [7 empty] | -24866.5803
-17920 | [7 empty] | -22562.487
-17300 | [7 empty] | -21781.8653
-12600 | [7 empty] | -15864.2487
-4290 | [7 empty] | -5401.399
-1490 | [7 empty] | -1876.0104
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
5950 | [7 empty] | 4473.5732
7620 | [7 empty] | 5729.1811
3200 | [7 empty] | 2405.9553
1060 | [7 empty] | 796.9727
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
1260 | [7 empty] | 947.3449
3960 | [7 empty] | 2977.3697
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
150 | [7 empty] | 112.7792
1280 | [7 empty] | 962.3821
2580 | [7 empty] | 1939.8015
3060 | [7 empty] | 2300.6948
2980 | [7 empty] | 2240.5459
2170 | [7 empty] | 1631.5385
35180 | [7 empty] | 26450.4715
26360 | [7 empty] | 19819.0571
21150 | [7 empty] | 15901.861
20130 | [7 empty] | 15134.9628
18580 | [7 empty] | 13969.5782
17930 | [7 empty] | 13480.8685
18800 | [7 empty] | 14134.9876
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
90 | [7 empty] | 67.6675
1810 | [7 empty] | 1360.8685
3580 | [7 empty] | 2691.6625
5850 | [7 empty] | 4398.3871
8110 | [7 empty] | 6097.5931
10080 | [7 empty] | 7578.7593
11410 | [7 empty] | 8578.7345
12330 | [7 empty] | 9270.4467
13020 | [7 empty] | 9789.2308
13560 | [7 empty] | 10195.2357
57880 | [7 empty] | 43517.7171
48060 | [7 empty] | 36134.4417
34970 | [7 empty] | 26292.5806
22610 | [7 empty] | 16999.5782
12810 | [7 empty] | 9631.34
6530 | [7 empty] | 4909.6526
2540 | [7 empty] | 1909.727
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
1560 | [7 empty] | 1172.9032
7780 | [7 empty] | 5849.4789
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
790 | [7 empty] | 593.9702
3090 | [7 empty] | 2323.2506
5390 | [7 empty] | 4052.531
7270 | [7 empty] | 5466.0298
48160 | [7 empty] | 36209.6278
39570 | [7 empty] | 29751.1414
23390 | [7 empty] | 17586.0298
7980 | [7 empty] | 5999.8511
20 | [7 empty] | 15.0372
0 | [7 empty] | 0
-40 | [7 empty] | -50.3627
-6600 | [7 empty] | -8309.8446
-12190 | [7 empty] | -15348.0311
-13950 | [7 empty] | -17563.9896
-11900 | [7 empty] | -14982.9016
-4710 | [7 empty] | -5930.2073
-240 | [7 empty] | -302.1762
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
26620 | [7 empty] | 20014.5409
20080 | [7 empty] | 15097.3697
8480 | [7 empty] | 6375.7816
0 | [7 empty] | 0
0 | [7 empty] | 0
-240 | [7 empty] | -302.1762
-10650 | [7 empty] | -13409.0674
-21350 | [7 empty] | -26881.0881
-27930 | [7 empty] | -35165.7513
-27250 | [7 empty] | -34309.5855
-24590 | [7 empty] | -30960.4663
-17040 | [7 empty] | -21454.5078
-7280 | [7 empty] | -9166.0104
-2360 | [7 empty] | -2971.399
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
10250 | [7 empty] | 7706.5757
7980 | [7 empty] | 5999.8511
20 | [7 empty] | 15.0372
0 | [7 empty] | 0
-3080 | [7 empty] | -3877.9275
-17560 | [7 empty] | -22109.2228
-25750 | [7 empty] | -32420.9845
-32400 | [7 empty] | -40793.7824
-36000 | [7 empty] | -45326.4249
-33990 | [7 empty] | -42795.6995
-30610 | [7 empty] | -38540.0518
-23410 | [7 empty] | -29474.7668
-13300 | [7 empty] | -16745.5959
-5640 | [7 empty] | -7101.1399
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-4500 | [7 empty] | -5665.8031
-430 | [7 empty] | -541.399
-2660 | [7 empty] | -3349.1192
-16480 | [7 empty] | -20749.4301
-28130 | [7 empty] | -35417.5648
-35940 | [7 empty] | -45250.8808
-43770 | [7 empty] | -55109.3782
-46710 | [7 empty] | -58811.0363
-47270 | [7 empty] | -59516.114
-46930 | [7 empty] | -59088.0311
-44740 | [7 empty] | -56330.6736
-36970 | [7 empty] | -46547.7202
-26980 | [7 empty] | -33969.6373
-19810 | [7 empty] | -24942.1244
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-6850 | [7 empty] | -8624.6114
0 | [7 empty] | 0
0 | [7 empty] | 0
-350 | [7 empty] | -440.6736
-3860 | [7 empty] | -4860
-12230 | [7 empty] | -15398.3938
-18040 | [7 empty] | -22713.5751
-18270 | [7 empty] | -23003.1606
-17730 | [7 empty] | -22323.2642
-13050 | [7 empty] | -16430.829
-8450 | [7 empty] | -10639.1192
-2050 | [7 empty] | -2581.0881
-920 | [7 empty] | -1158.342
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
1870 | [7 empty] | 1405.9801
4280 | [7 empty] | 3217.9653
4410 | [7 empty] | 3315.7072
5080 | [7 empty] | 3819.4541
5570 | [7 empty] | 4187.866
5350 | [7 empty] | 4022.4566
4410 | [7 empty] | 3315.7072
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
60 | [7 empty] | 45.1117
28470 | [7 empty] | 21405.4839
20290 | [7 empty] | 15255.2605
10770 | [7 empty] | 8097.5434
3580 | [7 empty] | 2691.6625
380 | [7 empty] | 285.7072
0 | [7 empty] | 0
0 | [7 empty] | 0
-250 | [7 empty] | -314.7668
-1050 | [7 empty] | -1322.0207
-1290 | [7 empty] | -1624.1969
-5710 | [7 empty] | -7189.2746
-2590 | [7 empty] | -3260.9845
-290 | [7 empty] | -365.1295
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
13880 | [7 empty] | 10435.8313
9600 | [7 empty] | 7217.866
1180 | [7 empty] | 887.196
0 | [7 empty] | 0
-730 | [7 empty] | -919.1192
-9450 | [7 empty] | -11898.1865
-24840 | [7 empty] | -31275.2332
-32040 | [7 empty] | -40340.5181
-36360 | [7 empty] | -45779.6891
-35690 | [7 empty] | -44936.114
-33410 | [7 empty] | -42065.4404
-25790 | [7 empty] | -32471.3472
-15870 | [7 empty] | -19981.399
-7330 | [7 empty] | -9228.9637
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-400 | [7 empty] | -503.6269
1370 | [7 empty] | 1030.0496
-230 | [7 empty] | -289.5855
-2020 | [7 empty] | -2543.3161
-18340 | [7 empty] | -23091.2953
-30690 | [7 empty] | -38640.7772
-39080 | [7 empty] | -49204.3523
-45780 | [7 empty] | -57640.1036
-49380 | [7 empty] | -62172.7461
-49740 | [7 empty] | -62626.0104
-45640 | [7 empty] | -57463.8342
-36960 | [7 empty] | -46535.1295
-24620 | [7 empty] | -30998.2383
-14880 | [7 empty] | -18734.9223
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-4590 | [7 empty] | -5779.1192
50 | [7 empty] | 37.5931
-1520 | [7 empty] | -1913.7824
-6720 | [7 empty] | -8460.9326
-22830 | [7 empty] | -28744.5078
-35390 | [7 empty] | -44558.3938
-44670 | [7 empty] | -56242.5389
-52360 | [7 empty] | -65924.7668
-56230 | [7 empty] | -70797.3575
-57030 | [7 empty] | -71804.6114
-54100 | [7 empty] | -68115.544
-44710 | [7 empty] | -56292.9016
-31290 | [7 empty] | -39396.2176
-21580 | [7 empty] | -27170.6736
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-7850 | [7 empty] | -9883.6788
-610 | [7 empty] | -768.0311
-1930 | [7 empty] | -2430
-9450 | [7 empty] | -11898.1865
-24670 | [7 empty] | -31061.1917
-34900 | [7 empty] | -43941.4508
-42690 | [7 empty] | -53749.5855
-49240 | [7 empty] | -61996.4767
-52280 | [7 empty] | -65824.0415
-52570 | [7 empty] | -66189.171
-47380 | [7 empty] | -59654.6114
-38510 | [7 empty] | -48486.6839
-27820 | [7 empty] | -35027.2539
-18700 | [7 empty] | -23544.5596
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-8910 | [7 empty] | -11218.2902
-1110 | [7 empty] | -1397.5648
-1000 | [7 empty] | -1259.0674
-940 | [7 empty] | -1183.5233
-910 | [7 empty] | -1145.7513
-1110 | [7 empty] | -1397.5648
-1220 | [7 empty] | -1536.0622
-1190 | [7 empty] | -1498.2902
-2050 | [7 empty] | -2581.0881
-1090 | [7 empty] | -1372.3834
-830 | [7 empty] | -1045.0259
-570 | [7 empty] | -717.6684
-300 | [7 empty] | -377.7202
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-2720 | [7 empty] | -3424.6632
-390 | [7 empty] | -491.0363
-10340 | [7 empty] | -13018.7565
-18630 | [7 empty] | -23456.4249
-25120 | [7 empty] | -31627.772
-28600 | [7 empty] | -36009.3264
-27380 | [7 empty] | -34473.2642
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-6040 | [7 empty] | -7604.7668
-520 | [7 empty] | -654.715
-3020 | [7 empty] | -3802.3834
-14630 | [7 empty] | -18420.1554
-30530 | [7 empty] | -38439.3264
-38020 | [7 empty] | -47869.7409
-46280 | [7 empty] | -58269.6373
-51220 | [7 empty] | -64489.4301
-50170 | [7 empty] | -63167.4093
-50620 | [7 empty] | -63733.9896
-47550 | [7 empty] | -59868.6528
-39180 | [7 empty] | -49330.2591
-30220 | [7 empty] | -38049.0155
-20640 | [7 empty] | -25987.1503
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-10610 | [7 empty] | -13358.7047
-3450 | [7 empty] | -4343.7824
-9440 | [7 empty] | -11885.5959
-18100 | [7 empty] | -22789.1192
-20640 | [7 empty] | -25987.1503
-28250 | [7 empty] | -35568.6528
-32890 | [7 empty] | -41410.7254
-37800 | [7 empty] | -47592.7461
-35460 | [7 empty] | -44646.5285
-32010 | [7 empty] | -40302.7461
-27890 | [7 empty] | -35115.3886
-23830 | [7 empty] | -30003.5751
-17720 | [7 empty] | -22310.6736
-10690 | [7 empty] | -13459.4301
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-8290 | [7 empty] | -10437.6684
-2640 | [7 empty] | -3323.9378
-8090 | [7 empty] | -10185.8549
-18160 | [7 empty] | -22864.6632
-32620 | [7 empty] | -41070.7772
-44910 | [7 empty] | -56544.715
-55480 | [7 empty] | -69853.057
-62780 | [7 empty] | -79044.2487
-65900 | [7 empty] | -82972.5389
-65990 | [7 empty] | -83085.8549
-61180 | [7 empty] | -77029.7409
-51680 | [7 empty] | -65068.601
-40370 | [7 empty] | -50828.5492
-30870 | [7 empty] | -38867.4093
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-20050 | [7 empty] | -25244.3005
-10570 | [7 empty] | -13308.342
-18950 | [7 empty] | -23859.3264
-25890 | [7 empty] | -32597.2539
-30010 | [7 empty] | -37784.6114
-33760 | [7 empty] | -42506.114
-37310 | [7 empty] | -46975.8031
-39570 | [7 empty] | -49821.2953
-41140 | [7 empty] | -51798.0311
-41050 | [7 empty] | -51684.715
-37940 | [7 empty] | -47769.0155
-30850 | [7 empty] | -38842.228
-23050 | [7 empty] | -29021.5026
-16400 | [7 empty] | -20648.7047
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-13020 | [7 empty] | -16393.057
-5860 | [7 empty] | -7378.1347
-14020 | [7 empty] | -17652.1244
-21870 | [7 empty] | -27535.8031
-30710 | [7 empty] | -38665.9585
-32260 | [7 empty] | -40617.513
-35430 | [7 empty] | -44608.7565
-43470 | [7 empty] | -54731.658
-39500 | [7 empty] | -49733.1606
-36200 | [7 empty] | -45578.2383
-29510 | [7 empty] | -37155.0777
-20170 | [7 empty] | -25395.3886
-9420 | [7 empty] | -11860.4145
-2340 | [7 empty] | -2946.2176
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
16400 | [7 empty] | 12330.5211
17880 | [7 empty] | 13443.2754
15700 | [7 empty] | 11804.2184
12950 | [7 empty] | 9736.6005
11050 | [7 empty] | 8308.0645
5230 | [7 empty] | 3932.2333
6350 | [7 empty] | 4774.3176
4870 | [7 empty] | 3661.5633
6990 | [7 empty] | 5255.5087
5590 | [7 empty] | 4202.9032
10730 | [7 empty] | 8067.469
14910 | [7 empty] | 11210.2481
19140 | [7 empty] | 14390.6203
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
1220 | [7 empty] | 917.2705
2920 | [7 empty] | 2195.4342
3990 | [7 empty] | 2999.9256
4730 | [7 empty] | 3556.3027
5370 | [7 empty] | 4037.4938
5990 | [7 empty] | 4503.6476
6600 | [7 empty] | 4962.2829
6970 | [7 empty] | 5240.4715
5820 | [7 empty] | 4375.8313
3730 | [7 empty] | 2804.4417
1700 | [7 empty] | 1278.1638
35280 | [7 empty] | 26525.6576
20310 | [7 empty] | 15270.2978
5830 | [7 empty] | 4383.3499
1890 | [7 empty] | 1421.0174
1010 | [7 empty] | 759.3797
580 | [7 empty] | 436.0794
270 | [7 empty] | 203.0025
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
150 | [7 empty] | 112.7792
1450 | [7 empty] | 1090.1985
3120 | [7 empty] | 2345.8065
4830 | [7 empty] | 3631.4888
7660 | [7 empty] | 5759.2556
50340 | [7 empty] | 37848.6849
39730 | [7 empty] | 29871.4392
20740 | [7 empty] | 15593.598
4930 | [7 empty] | 3706.6749
0 | [7 empty] | 0
0 | [7 empty] | 0
-1570 | [7 empty] | -1976.7358
-9920 | [7 empty] | -12489.9482
-13730 | [7 empty] | -17286.9948
-15630 | [7 empty] | -19679.2228
-13370 | [7 empty] | -16833.7306
-7410 | [7 empty] | -9329.6891
-1010 | [7 empty] | -1271.658
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
21860 | [7 empty] | 16435.6824
13010 | [7 empty] | 9781.7122
2060 | [7 empty] | 1548.8337
0 | [7 empty] | 0
0 | [7 empty] | 0
-10620 | [7 empty] | -13371.2953
-24220 | [7 empty] | -30494.6114
-35210 | [7 empty] | -44331.7617
-41990 | [7 empty] | -52868.2383
-41440 | [7 empty] | -52175.7513
-38790 | [7 empty] | -48839.2228
-31050 | [7 empty] | -39094.0415
-20840 | [7 empty] | -26238.9637
-10400 | [7 empty] | -13094.3005
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-4610 | [7 empty] | -5804.3005
0 | [7 empty] | 0
-1910 | [7 empty] | -2404.8187
-9090 | [7 empty] | -11444.9223
-19700 | [7 empty] | -24803.6269
-24740 | [7 empty] | -31149.3264
-24250 | [7 empty] | -30532.3834
-24770 | [7 empty] | -31187.0984
-23840 | [7 empty] | -30016.1658
-28790 | [7 empty] | -36248.5492
-27450 | [7 empty] | -34561.399
-18100 | [7 empty] | -22789.1192
-6920 | [7 empty] | -8712.7461
-1330 | [7 empty] | -1674.5596
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
12700 | [7 empty] | 9548.6352
8180 | [7 empty] | 6150.2233
240 | [7 empty] | 180.4467
-650 | [7 empty] | -818.3938
-5740 | [7 empty] | -7227.0466
-18870 | [7 empty] | -23758.601
-29960 | [7 empty] | -37721.658
-36810 | [7 empty] | -46346.2694
-41270 | [7 empty] | -51961.7098
-42080 | [7 empty] | -52981.5544
-37850 | [7 empty] | -47655.6995
-29710 | [7 empty] | -37406.8912
-18750 | [7 empty] | -23607.513
-8750 | [7 empty] | -11016.8394
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-3920 | [7 empty] | -4935.544
0 | [7 empty] | 0
-1710 | [7 empty] | -2153.0052
-16120 | [7 empty] | -20296.1658
-32150 | [7 empty] | -40479.0155
-43540 | [7 empty] | -54819.7927
-52420 | [7 empty] | -66000.3109
-57390 | [7 empty] | -72257.8756
-60510 | [7 empty] | -76186.1658
-60590 | [7 empty] | -76286.8912
-55350 | [7 empty] | -69689.3782
-44790 | [7 empty] | -56393.6269
-33040 | [7 empty] | -41599.5855
-20810 | [7 empty] | -26201.1917
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-11430 | [7 empty] | -14391.1399
-5110 | [7 empty] | -6433.8342
-8550 | [7 empty] | -10765.0259
-10570 | [7 empty] | -13308.342
-14580 | [7 empty] | -18357.2021
-20600 | [7 empty] | -25936.7876
-24120 | [7 empty] | -30368.7047
-26980 | [7 empty] | -33969.6373
-29490 | [7 empty] | -37129.8964
-29310 | [7 empty] | -36903.2642
-25130 | [7 empty] | -31640.3627
-20410 | [7 empty] | -25697.5648
-16440 | [7 empty] | -20699.0674
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-8180 | [7 empty] | -10299.171
-3190 | [7 empty] | -4016.4249
-7390 | [7 empty] | -9304.5078
-12280 | [7 empty] | -15461.3472
-13340 | [7 empty] | -16795.9585
-11630 | [7 empty] | -14642.9534
-7640 | [7 empty] | -9619.2746
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
16720 | [7 empty] | 12571.1166
13980 | [7 empty] | 10511.0174
4130 | [7 empty] | 3105.1861
0 | [7 empty] | 0
-160 | [7 empty] | -201.4508
-5510 | [7 empty] | -6937.4611
-14900 | [7 empty] | -18760.1036
-22890 | [7 empty] | -28820.0518
-29170 | [7 empty] | -36726.9948
-30740 | [7 empty] | -38703.7306
-26150 | [7 empty] | -32924.6114
-17690 | [7 empty] | -22272.9016
-6380 | [7 empty] | -8032.8497
-880 | [7 empty] | -1107.9793
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
16000 | [7 empty] | 12029.7767
11000 | [7 empty] | 8270.4715
1080 | [7 empty] | 812.0099
-120 | [7 empty] | -151.0881
-5460 | [7 empty] | -6874.5078
-18370 | [7 empty] | -23129.0674
-29200 | [7 empty] | -36764.7668
-37750 | [7 empty] | -47529.7927
-39070 | [7 empty] | -49191.7617
-40220 | [7 empty] | -50639.6891
-38640 | [7 empty] | -48650.3627
-31360 | [7 empty] | -39484.3523
-20960 | [7 empty] | -26390.0518
-9630 | [7 empty] | -12124.8187
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-3020 | [7 empty] | -3802.3834
-280 | [7 empty] | -352.5389
-1700 | [7 empty] | -2140.4145
-7100 | [7 empty] | -8939.3782
-15880 | [7 empty] | -19993.9896
-21700 | [7 empty] | -27321.7617
-23410 | [7 empty] | -29474.7668
-27450 | [7 empty] | -34561.399
-29650 | [7 empty] | -37331.3472
-31080 | [7 empty] | -39131.8135
-30050 | [7 empty] | -37834.9741
-24790 | [7 empty] | -31212.2798
-18010 | [7 empty] | -22675.8031
-11310 | [7 empty] | -14240.0518
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-11640 | [7 empty] | -14655.544
-7830 | [7 empty] | -9858.4974
-16400 | [7 empty] | -20648.7047
-25920 | [7 empty] | -32635.0259
-38670 | [7 empty] | -48688.1347
-50200 | [7 empty] | -63205.1813
-56900 | [7 empty] | -71640.9326
-62510 | [7 empty] | -78704.3005
-61930 | [7 empty] | -77974.0415
-59290 | [7 empty] | -74650.1036
-56470 | [7 empty] | -71099.5337
-49530 | [7 empty] | -62361.6062
-38390 | [7 empty] | -48335.5959
-27500 | [7 empty] | -34624.3523
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-30360 | [7 empty] | -38225.285
-21070 | [7 empty] | -26528.5492
-30140 | [7 empty] | -37948.2902
-36460 | [7 empty] | -45905.5959
-47220 | [7 empty] | -59453.1606
-53660 | [7 empty] | -67561.5544
-54710 | [7 empty] | -68883.5751
-65820 | [7 empty] | -82871.8135
-67180 | [7 empty] | -84584.1451
-68990 | [7 empty] | -86863.057
-64080 | [7 empty] | -80681.0363
-55130 | [7 empty] | -69412.3834
-45210 | [7 empty] | -56922.4352
-34490 | [7 empty] | -43425.2332
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-37740 | [7 empty] | -47517.2021
-24780 | [7 empty] | -31199.6891
-28180 | [7 empty] | -35480.5181
-35360 | [7 empty] | -44520.6218
-46300 | [7 empty] | -58294.8187
-52070 | [7 empty] | -65559.6373
-56750 | [7 empty] | -71452.0725
-56060 | [7 empty] | -70583.3161
-56920 | [7 empty] | -71666.114
-53530 | [7 empty] | -67397.8756
-46050 | [7 empty] | -57980.0518
-38220 | [7 empty] | -48121.5544
-30300 | [7 empty] | -38149.7409
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-70940 | [7 empty] | -89318.2383
-56010 | [7 empty] | -70520.3627
-58020 | [7 empty] | -73051.0881
-60150 | [7 empty] | -75732.9016
-62080 | [7 empty] | -78162.9016
-60820 | [7 empty] | -76576.4767
-55420 | [7 empty] | -69777.513
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-50800 | [7 empty] | -63960.6218
-32860 | [7 empty] | -41372.9534
-40470 | [7 empty] | -50954.456
-48290 | [7 empty] | -60800.3627
-50540 | [7 empty] | -63633.2642
-56330 | [7 empty] | -70923.2642
-63810 | [7 empty] | -80341.0881
-70540 | [7 empty] | -88814.6114
-74300 | [7 empty] | -93548.7047
-73490 | [7 empty] | -92528.8601
-68390 | [7 empty] | -86107.6166
-59860 | [7 empty] | -75367.772
-48310 | [7 empty] | -60825.544
-36740 | [7 empty] | -46258.1347
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-27390 | [7 empty] | -34485.8549
-15000 | [7 empty] | -18886.0104
-26730 | [7 empty] | -33654.8705
-37860 | [7 empty] | -47668.2902
-46680 | [7 empty] | -58773.2642
-54610 | [7 empty] | -68757.6684
-61160 | [7 empty] | -77004.5596
-67030 | [7 empty] | -84395.285
-69610 | [7 empty] | -87643.6788
-69250 | [7 empty] | -87190.4145
-64430 | [7 empty] | -81121.7098
-55610 | [7 empty] | -70016.7358
-43780 | [7 empty] | -55121.9689
-32780 | [7 empty] | -41272.228
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-20890 | [7 empty] | -26301.9171
-12120 | [7 empty] | -15259.8964
-27430 | [7 empty] | -34536.2176
-41950 | [7 empty] | -52817.8756
-52530 | [7 empty] | -66138.8083
-58530 | [7 empty] | -73693.2124
-64160 | [7 empty] | -80781.7617
-68000 | [7 empty] | -85616.5803
-68930 | [7 empty] | -86787.513
-68680 | [7 empty] | -86472.7461
-63800 | [7 empty] | -80328.4974
-53720 | [7 empty] | -67637.0984
-42350 | [7 empty] | -53321.5026
-31910 | [7 empty] | -40176.8394
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-20980 | [7 empty] | -26415.2332
-13550 | [7 empty] | -17060.3627
-28110 | [7 empty] | -35392.3834
-41690 | [7 empty] | -52490.5181
-51300 | [7 empty] | -64590.1554
-52650 | [7 empty] | -66289.8964
-56960 | [7 empty] | -71716.4767
-62470 | [7 empty] | -78653.9378
-67410 | [7 empty] | -84873.7306
-65130 | [7 empty] | -82003.057
-62100 | [7 empty] | -78188.0829
-54360 | [7 empty] | -68442.9016
-43360 | [7 empty] | -54593.1606
-32090 | [7 empty] | -40403.4715
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-26930 | [7 empty] | -33906.6839
-19770 | [7 empty] | -24891.7617
-35940 | [7 empty] | -45250.8808
-47850 | [7 empty] | -60246.3731
-52880 | [7 empty] | -66579.4819
-57540 | [7 empty] | -72446.7358
-61060 | [7 empty] | -76878.6528
-67800 | [7 empty] | -85364.7668
-71030 | [7 empty] | -89431.5544
-73160 | [7 empty] | -92113.3679
-68440 | [7 empty] | -86170.5699
-58900 | [7 empty] | -74159.0674
-47060 | [7 empty] | -59251.7098
-35120 | [7 empty] | -44218.4456
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-36580 | [7 empty] | -46056.6839
-24120 | [7 empty] | -30368.7047
-31940 | [7 empty] | -40214.6114
-37690 | [7 empty] | -47454.2487
-48330 | [7 empty] | -60850.7254
-51950 | [7 empty] | -65408.5492
-58930 | [7 empty] | -74196.8394
-54980 | [7 empty] | -69223.5233
-50890 | [7 empty] | -64073.9378
-44100 | [7 empty] | -55524.8705
-38540 | [7 empty] | -48524.456
-30440 | [7 empty] | -38326.0104
-20660 | [7 empty] | -26012.3316
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-15010 | [7 empty] | -18898.601
-8100 | [7 empty] | -10198.4456
-17320 | [7 empty] | -21807.0466
-24740 | [7 empty] | -31149.3264
-30180 | [7 empty] | -37998.6528
-32230 | [7 empty] | -40579.7409
-31930 | [7 empty] | -40202.0207
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-7540 | [7 empty] | -9493.3679
-2200 | [7 empty] | -2769.9482
-15410 | [7 empty] | -19402.228
-33030 | [7 empty] | -41586.9948
-45220 | [7 empty] | -56935.0259
-55620 | [7 empty] | -70029.3264
-63760 | [7 empty] | -80278.1347
-70570 | [7 empty] | -88852.3834
-73470 | [7 empty] | -92503.6788
-73610 | [7 empty] | -92679.9482
-69330 | [7 empty] | -87291.1399
-59640 | [7 empty] | -75090.7772
-46110 | [7 empty] | -58055.5959
-32470 | [7 empty] | -40881.9171
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-15580 | [7 empty] | -19616.2694
-10680 | [7 empty] | -13446.8394
-25800 | [7 empty] | -32483.9378
-38180 | [7 empty] | -48071.1917
-47270 | [7 empty] | -59516.114
-55300 | [7 empty] | -69626.4249
-61270 | [7 empty] | -77143.057
-66280 | [7 empty] | -83450.9845
-68190 | [7 empty] | -85855.8031
-66940 | [7 empty] | -84281.9689
-61880 | [7 empty] | -77911.0881
-52110 | [7 empty] | -65610
-39350 | [7 empty] | -49544.3005
-27440 | [7 empty] | -34548.8083
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-10460 | [7 empty] | -13169.8446
-1620 | [7 empty] | -2039.6891
-9330 | [7 empty] | -11747.0984
-25920 | [7 empty] | -32635.0259
-37710 | [7 empty] | -47479.4301
-43530 | [7 empty] | -54807.2021
-49640 | [7 empty] | -62500.1036
-52320 | [7 empty] | -65874.4041
-52010 | [7 empty] | -65484.0933
-50810 | [7 empty] | -63973.2124
-44380 | [7 empty] | -55877.4093
-35840 | [7 empty] | -45124.9741
-23950 | [7 empty] | -30154.6632
-12790 | [7 empty] | -16103.4715
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-4760 | [7 empty] | -5993.1606
-360 | [7 empty] | -453.2642
-1870 | [7 empty] | -2354.456
-10270 | [7 empty] | -12930.6218
-24960 | [7 empty] | -31426.3212
-33990 | [7 empty] | -42795.6995
-39850 | [7 empty] | -50173.8342
-46110 | [7 empty] | -58055.5959
-50100 | [7 empty] | -63079.2746
-51130 | [7 empty] | -64376.114
-48010 | [7 empty] | -60447.8238
-39440 | [7 empty] | -49657.6166
-28410 | [7 empty] | -35770.1036
-17830 | [7 empty] | -22449.171
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-5820 | [7 empty] | -7327.772
-920 | [7 empty] | -1158.342
-5330 | [7 empty] | -6710.829
-21970 | [7 empty] | -27661.7098
-33830 | [7 empty] | -42594.2487
-42710 | [7 empty] | -53774.7668
-48540 | [7 empty] | -61115.1295
-54190 | [7 empty] | -68228.8601
-56750 | [7 empty] | -71452.0725
-56620 | [7 empty] | -71288.3938
-53600 | [7 empty] | -67486.0104
-45280 | [7 empty] | -57010.5699
-33250 | [7 empty] | -41863.9896
-20800 | [7 empty] | -26188.601
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-7570 | [7 empty] | -9531.1399
-2320 | [7 empty] | -2921.0363
-8610 | [7 empty] | -10840.5699
-16730 | [7 empty] | -21064.1969
-19720 | [7 empty] | -24828.8083
-22880 | [7 empty] | -28807.4611
-35910 | [7 empty] | -45213.1088
-36820 | [7 empty] | -46358.8601
-30100 | [7 empty] | -37897.9275
-25940 | [7 empty] | -32660.2073
-21820 | [7 empty] | -27472.8497
-16110 | [7 empty] | -20283.5751
-11120 | [7 empty] | -14000.829
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-32020 | [7 empty] | -40315.3368
-29320 | [7 empty] | -36915.8549
-33700 | [7 empty] | -42430.5699
-34010 | [7 empty] | -42820.8808
-34790 | [7 empty] | -43802.9534
-34960 | [7 empty] | -44016.9948
-30330 | [7 empty] | -38187.513
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-11550 | [7 empty] | -14542.228
-5360 | [7 empty] | -6748.601
-14060 | [7 empty] | -17702.487
-23550 | [7 empty] | -29651.0363
-35470 | [7 empty] | -44659.1192
-43160 | [7 empty] | -54341.3472
-53770 | [7 empty] | -67700.0518
-54180 | [7 empty] | -68216.2694
-56540 | [7 empty] | -71187.6684
-58870 | [7 empty] | -74121.2953
-54800 | [7 empty] | -68996.8912
-48030 | [7 empty] | -60473.0052
-36790 | [7 empty] | -46321.0881
-25340 | [7 empty] | -31904.7668
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-19710 | [7 empty] | -24816.2176
-14000 | [7 empty] | -17626.943
-28880 | [7 empty] | -36361.8653
-39500 | [7 empty] | -49733.1606
-46040 | [7 empty] | -57967.4611
-52120 | [7 empty] | -65622.5907
-53670 | [7 empty] | -67574.1451
-56670 | [7 empty] | -71351.3472
-55130 | [7 empty] | -69412.3834
-54760 | [7 empty] | -68946.5285
-49510 | [7 empty] | -62336.4249
-43140 | [7 empty] | -54316.1658
-35540 | [7 empty] | -44747.2539
-28050 | [7 empty] | -35316.8394
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-29300 | [7 empty] | -36890.6736
-16180 | [7 empty] | -20371.7098
-22850 | [7 empty] | -28769.6891
-27490 | [7 empty] | -34611.7617
-31630 | [7 empty] | -39824.3005
-33180 | [7 empty] | -41775.8549
-36640 | [7 empty] | -46132.228
-41600 | [7 empty] | -52377.2021
-42030 | [7 empty] | -52918.601
-41880 | [7 empty] | -52729.7409
-39090 | [7 empty] | -49216.943
-33160 | [7 empty] | -41750.6736
-26300 | [7 empty] | -33113.4715
-19990 | [7 empty] | -25168.7565
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-22260 | [7 empty] | -28026.8394
-14070 | [7 empty] | -17715.0777
-25930 | [7 empty] | -32647.6166
-33300 | [7 empty] | -41926.943
-39650 | [7 empty] | -49922.0207
-46750 | [7 empty] | -58861.399
-55600 | [7 empty] | -70004.1451
-58410 | [7 empty] | -73542.1244
-62060 | [7 empty] | -78137.7202
-61650 | [7 empty] | -77621.5026
-57730 | [7 empty] | -72685.9585
-49020 | [7 empty] | -61719.4819
-38640 | [7 empty] | -48650.3627
-28600 | [7 empty] | -36009.3264
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-19560 | [7 empty] | -24627.3575
-9710 | [7 empty] | -12225.544
-22440 | [7 empty] | -28253.4715
-34770 | [7 empty] | -43777.772
-44150 | [7 empty] | -55587.8238
-51630 | [7 empty] | -65005.6477
-56970 | [7 empty] | -71729.0674
-61530 | [7 empty] | -77470.4145
-63450 | [7 empty] | -79887.8238
-62700 | [7 empty] | -78943.5233
-58060 | [7 empty] | -73101.4508
-49350 | [7 empty] | -62134.9741
-38510 | [7 empty] | -48486.6839
-28000 | [7 empty] | -35253.886
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-18320 | [7 empty] | -23066.114
-15670 | [7 empty] | -19729.5855
-26080 | [7 empty] | -32836.4767
-34910 | [7 empty] | -43954.0415
-42900 | [7 empty] | -54013.9896
-49310 | [7 empty] | -62084.6114
-53380 | [7 empty] | -67209.0155
-55650 | [7 empty] | -70067.0984
-55110 | [7 empty] | -69387.2021
-51350 | [7 empty] | -64653.1088
-44450 | [7 empty] | -55965.544
-36340 | [7 empty] | -45754.5078
-28890 | [7 empty] | -36374.456
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-65690 | [7 empty] | -82708.1347
-52390 | [7 empty] | -65962.5389
-56290 | [7 empty] | -70872.9016
-59270 | [7 empty] | -74624.9223
-58660 | [7 empty] | -73856.8912
-56970 | [7 empty] | -71729.0674
-52270 | [7 empty] | -65811.4508
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-45810 | [7 empty] | -57677.8756
-32020 | [7 empty] | -40315.3368
-45380 | [7 empty] | -57136.4767
-57600 | [7 empty] | -72522.2798
-68300 | [7 empty] | -85994.3005
-70480 | [7 empty] | -88739.0674
-77150 | [7 empty] | -97137.0466
-77630 | [7 empty] | -97741.399
-69860 | [7 empty] | -87958.4456
-70010 | [7 empty] | -88147.3057
-61270 | [7 empty] | -77143.057
-51140 | [7 empty] | -64388.7047
-41560 | [7 empty] | -52326.8394
-33300 | [7 empty] | -41926.943
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-43320 | [7 empty] | -54542.7979
-22710 | [7 empty] | -28593.4197
-27060 | [7 empty] | -34070.3627
-31200 | [7 empty] | -39282.9016
-37980 | [7 empty] | -47819.3782
-40620 | [7 empty] | -51143.3161
-41270 | [7 empty] | -51961.7098
-43450 | [7 empty] | -54706.4767
-43280 | [7 empty] | -54492.4352
-40120 | [7 empty] | -50513.7824
-34050 | [7 empty] | -42871.2435
-27160 | [7 empty] | -34196.2694
-19350 | [7 empty] | -24362.9534
-11790 | [7 empty] | -14844.4041
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-10190 | [7 empty] | -12829.8964
-2610 | [7 empty] | -3286.1658
-7100 | [7 empty] | -8939.3782
-11280 | [7 empty] | -14202.2798
-15880 | [7 empty] | -19993.9896
-19080 | [7 empty] | -24023.0052
-21070 | [7 empty] | -26528.5492
-23570 | [7 empty] | -29676.2176
-27570 | [7 empty] | -34712.487
-27630 | [7 empty] | -34788.0311
-25120 | [7 empty] | -31627.772
-19410 | [7 empty] | -24438.4974
-12690 | [7 empty] | -15977.5648
-6490 | [7 empty] | -8171.3472
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-9400 | [7 empty] | -11835.2332
-5330 | [7 empty] | -6710.829
-14910 | [7 empty] | -18772.6943
-23390 | [7 empty] | -29449.5855
-29910 | [7 empty] | -37658.7047
-35030 | [7 empty] | -44105.1295
-37580 | [7 empty] | -47315.7513
-47870 | [7 empty] | -60271.5544
-48960 | [7 empty] | -61643.9378
-47880 | [7 empty] | -60284.1451
-40750 | [7 empty] | -51306.9948
-34760 | [7 empty] | -43765.1813
-27920 | [7 empty] | -35153.1606
-21710 | [7 empty] | -27334.3523
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-22650 | [7 empty] | -28517.8756
-14940 | [7 empty] | -18810.4663
-24350 | [7 empty] | -30658.2902
-33170 | [7 empty] | -41763.2642
-39110 | [7 empty] | -49242.1244
-43450 | [7 empty] | -54706.4767
-45280 | [7 empty] | -57010.5699
-56010 | [7 empty] | -70520.3627
-63040 | [7 empty] | -79371.6062
-63140 | [7 empty] | -79497.513
-59760 | [7 empty] | -75241.8653
-53470 | [7 empty] | -67322.3316
-43440 | [7 empty] | -54693.886
-34220 | [7 empty] | -43085.285
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-46180 | [7 empty] | -58143.7306
-35860 | [7 empty] | -45150.1554
-44290 | [7 empty] | -55764.0933
-53170 | [7 empty] | -66944.6114
-60500 | [7 empty] | -76173.5751
-65320 | [7 empty] | -82242.2798
-70160 | [7 empty] | -88336.1658
-68870 | [7 empty] | -86711.9689
-62180 | [7 empty] | -78288.8083
-62730 | [7 empty] | -78981.2953
-54650 | [7 empty] | -68808.0311
-47600 | [7 empty] | -59931.6062
-41240 | [7 empty] | -51923.9378
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-84030 | [7 empty] | -105799.4301
-64730 | [7 empty] | -81499.4301
-66330 | [7 empty] | -83513.9378
-68550 | [7 empty] | -86309.0674
-68510 | [7 empty] | -86258.7047
-66550 | [7 empty] | -83790.9326
-61670 | [7 empty] | -77646.6839
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-72510 | [7 empty] | -91294.9741
-47490 | [7 empty] | -59793.1088
-57050 | [7 empty] | -71829.7927
-69880 | [7 empty] | -87983.6269
-78310 | [7 empty] | -98597.5648
-85950 | [7 empty] | -108216.8394
-91060 | [7 empty] | -114650.6736
-95110 | [7 empty] | -119749.8964
-95930 | [7 empty] | -120782.3316
-93150 | [7 empty] | -117282.1244
-88130 | [7 empty] | -110961.6062
-79550 | [7 empty] | -100158.8083
-68020 | [7 empty] | -85641.7617
-57370 | [7 empty] | -72232.6943
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-72680 | [7 empty] | -91509.0155
-49170 | [7 empty] | -61908.342
-58680 | [7 empty] | -73882.0725
-68930 | [7 empty] | -86787.513
-77380 | [7 empty] | -97426.6321
-84020 | [7 empty] | -105786.8394
-88450 | [7 empty] | -111364.5078
-91170 | [7 empty] | -114789.171
-90970 | [7 empty] | -114537.3575
-87900 | [7 empty] | -110672.0207
-83730 | [7 empty] | -105421.7098
-74290 | [7 empty] | -93536.114
-62120 | [7 empty] | -78213.2642
-50370 | [7 empty] | -63419.2228
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-48840 | [7 empty] | -61492.8497
-31440 | [7 empty] | -39585.0777
-44050 | [7 empty] | -55461.9171
-55860 | [7 empty] | -70331.5026
-64890 | [7 empty] | -81700.8808
-71960 | [7 empty] | -90602.487
-77020 | [7 empty] | -96973.3679
-81790 | [7 empty] | -102979.1192
-82870 | [7 empty] | -104338.9119
-81230 | [7 empty] | -102274.0415
-76320 | [7 empty] | -96092.0207
-65620 | [7 empty] | -82620
-54110 | [7 empty] | -68128.1347
-43820 | [7 empty] | -55172.3316
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-43520 | [7 empty] | -54794.6114
-24530 | [7 empty] | -30884.9223
-38200 | [7 empty] | -48096.3731
-43760 | [7 empty] | -55096.7876
-46180 | [7 empty] | -58143.7306
-50560 | [7 empty] | -63658.4456
-57570 | [7 empty] | -72484.5078
-58260 | [7 empty] | -73353.2642
-53340 | [7 empty] | -67158.6528
-54090 | [7 empty] | -68102.9534
-47550 | [7 empty] | -59868.6528
-39680 | [7 empty] | -49959.7927
-30010 | [7 empty] | -37784.6114
-21930 | [7 empty] | -27611.3472
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-19640 | [7 empty] | -24728.0829
-12410 | [7 empty] | -15625.0259
-22320 | [7 empty] | -28102.3834
-33850 | [7 empty] | -42619.4301
-43190 | [7 empty] | -54379.1192
-51420 | [7 empty] | -64741.2435
-57340 | [7 empty] | -72194.9223
-62140 | [7 empty] | -78238.4456
-66100 | [7 empty] | -83224.3523
-66060 | [7 empty] | -83173.9896
-60830 | [7 empty] | -76589.0674
-52520 | [7 empty] | -66126.2176
-41870 | [7 empty] | -52717.1503
-31060 | [7 empty] | -39106.6321
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-24650 | [7 empty] | -31036.0104
-21190 | [7 empty] | -26679.6373
-31120 | [7 empty] | -39182.1762
-38920 | [7 empty] | -49002.9016
-47250 | [7 empty] | -59490.9326
-53230 | [7 empty] | -67020.1554
-53160 | [7 empty] | -66932.0207
-56230 | [7 empty] | -70797.3575
-52830 | [7 empty] | -66516.5285
-48920 | [7 empty] | -61593.5751
-42560 | [7 empty] | -53585.9067
-35390 | [7 empty] | -44558.3938
-29220 | [7 empty] | -36789.9482
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-71430 | [7 empty] | -89935.1813
-54880 | [7 empty] | -69097.6166
-50420 | [7 empty] | -63482.1762
-51740 | [7 empty] | -65144.1451
-51580 | [7 empty] | -64942.6943
-52120 | [7 empty] | -65622.5907
-49580 | [7 empty] | -62424.5596
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-53420 | [7 empty] | -67259.3782
-38170 | [7 empty] | -48058.601
-50470 | [7 empty] | -63545.1295
-62240 | [7 empty] | -78364.3523
-70470 | [7 empty] | -88726.4767
-77860 | [7 empty] | -98030.9845
-78710 | [7 empty] | -99101.1917
-85530 | [7 empty] | -107688.0311
-87120 | [7 empty] | -109689.9482
-86930 | [7 empty] | -109450.7254
-81810 | [7 empty] | -103004.3005
-69740 | [7 empty] | -87807.3575
-59780 | [7 empty] | -75267.0466
-50940 | [7 empty] | -64136.8912
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-61600 | [7 empty] | -77558.5492
-40160 | [7 empty] | -50564.1451
-51530 | [7 empty] | -64879.7409
-62380 | [7 empty] | -78540.6218
-66930 | [7 empty] | -84269.3782
-73070 | [7 empty] | -92000.0518
-75360 | [7 empty] | -94883.3161
-80650 | [7 empty] | -101543.7824
-79590 | [7 empty] | -100209.171
-69910 | [7 empty] | -88021.399
-63570 | [7 empty] | -80038.9119
-58450 | [7 empty] | -73592.487
-48910 | [7 empty] | -61580.9845
-39030 | [7 empty] | -49141.399
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-51380 | [7 empty] | -64690.8808
-35100 | [7 empty] | -44193.2642
-43780 | [7 empty] | -55121.9689
-56270 | [7 empty] | -70847.7202
-62920 | [7 empty] | -79220.5181
-68690 | [7 empty] | -86485.3368
-73200 | [7 empty] | -92163.7306
-75010 | [7 empty] | -94442.6425
-75160 | [7 empty] | -94631.5026
-71500 | [7 empty] | -90023.3161
-61990 | [7 empty] | -78049.5855
-51090 | [7 empty] | -64325.7513
-38970 | [7 empty] | -49065.8549
-29270 | [7 empty] | -36852.9016
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-25610 | [7 empty] | -32244.715
-17560 | [7 empty] | -22109.2228
-31260 | [7 empty] | -39358.4456
-42720 | [7 empty] | -53787.3575
-52250 | [7 empty] | -65786.2694
-60750 | [7 empty] | -76488.342
-66790 | [7 empty] | -84093.1088
-72660 | [7 empty] | -91483.8342
-71550 | [7 empty] | -90086.2694
-70750 | [7 empty] | -89079.0155
-65950 | [7 empty] | -83035.4922
-58060 | [7 empty] | -73101.4508
-47580 | [7 empty] | -59906.4249
-36590 | [7 empty] | -46069.2746
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-26660 | [7 empty] | -33566.7358
-18140 | [7 empty] | -22839.4819
-32210 | [7 empty] | -40554.5596
-41370 | [7 empty] | -52087.6166
-50500 | [7 empty] | -63582.9016
-56100 | [7 empty] | -70633.6788
-60760 | [7 empty] | -76500.9326
-62500 | [7 empty] | -78691.7098
-66930 | [7 empty] | -84269.3782
-68340 | [7 empty] | -86044.6632
-64040 | [7 empty] | -80630.6736
-56900 | [7 empty] | -71640.9326
-47100 | [7 empty] | -59302.0725
-37300 | [7 empty] | -46963.2124
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-42400 | [7 empty] | -53384.456
-34270 | [7 empty] | -43148.2383
-44360 | [7 empty] | -55852.228
-50970 | [7 empty] | -64174.6632
-58440 | [7 empty] | -73579.8964
-63190 | [7 empty] | -79560.4663
-65020 | [7 empty] | -81864.5596
-66260 | [7 empty] | -83425.8031
-66110 | [7 empty] | -83236.943
-62520 | [7 empty] | -78716.8912
-55800 | [7 empty] | -70255.9585
-47620 | [7 empty] | -59956.7876
-39110 | [7 empty] | -49242.1244
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-83960 | [7 empty] | -105711.2953
-64830 | [7 empty] | -81625.3368
-63090 | [7 empty] | -79434.5596
-67530 | [7 empty] | -85024.8187
-68130 | [7 empty] | -85780.2591
-64340 | [7 empty] | -81008.3938
-60110 | [7 empty] | -75682.5389
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-66510 | [7 empty] | -83740.5699
-43780 | [7 empty] | -55121.9689
-49880 | [7 empty] | -62802.2798
-57200 | [7 empty] | -72018.6528
-66620 | [7 empty] | -83879.0674
-76830 | [7 empty] | -96734.1451
-81310 | [7 empty] | -102374.7668
-80630 | [7 empty] | -101518.601
-81410 | [7 empty] | -102500.6736
-82790 | [7 empty] | -104238.1865
-78700 | [7 empty] | -99088.601
-68820 | [7 empty] | -86649.0155
-57760 | [7 empty] | -72723.7306
-46870 | [7 empty] | -59012.487
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-57290 | [7 empty] | -72131.9689
-33540 | [7 empty] | -42229.1192
-38100 | [7 empty] | -47970.4663
-45470 | [7 empty] | -57249.7927
-54460 | [7 empty] | -68568.8083
-54030 | [7 empty] | -68027.4093
-55340 | [7 empty] | -69676.7876
-67130 | [7 empty] | -84521.1917
-62930 | [7 empty] | -79233.1088
-66430 | [7 empty] | -83639.8446
-65100 | [7 empty] | -81965.285
-56200 | [7 empty] | -70759.5855
-46460 | [7 empty] | -58496.2694
-36790 | [7 empty] | -46321.0881
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-44770 | [7 empty] | -56368.4456
-33690 | [7 empty] | -42417.9793
-47360 | [7 empty] | -59629.4301
-60110 | [7 empty] | -75682.5389
-68070 | [7 empty] | -85704.715
-76850 | [7 empty] | -96759.3264
-81030 | [7 empty] | -102022.228
-85770 | [7 empty] | -107990.2073
-86860 | [7 empty] | -109362.5907
-85920 | [7 empty] | -108179.0674
-80320 | [7 empty] | -101128.2902
-69970 | [7 empty] | -88096.943
-60240 | [7 empty] | -75846.2176
-50520 | [7 empty] | -63608.0829
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-64700 | [7 empty] | -81461.658
-43980 | [7 empty] | -55373.7824
-48710 | [7 empty] | -61329.171
-59620 | [7 empty] | -75065.5959
-60630 | [7 empty] | -76337.2539
-65320 | [7 empty] | -82242.2798
-75660 | [7 empty] | -95261.0363
-79020 | [7 empty] | -99491.5026
-84200 | [7 empty] | -106013.4715
-82080 | [7 empty] | -103344.2487
-78590 | [7 empty] | -98950.1036
-71710 | [7 empty] | -90287.7202
-60460 | [7 empty] | -76123.2124
-49120 | [7 empty] | -61845.3886
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-61540 | [7 empty] | -77483.0052
-38450 | [7 empty] | -48411.1399
-44570 | [7 empty] | -56116.6321
-50210 | [7 empty] | -63217.772
-53560 | [7 empty] | -67435.6477
-57840 | [7 empty] | -72824.456
-61320 | [7 empty] | -77206.0104
-69810 | [7 empty] | -87895.4922
-69460 | [7 empty] | -87454.8187
-74520 | [7 empty] | -93825.6995
-72130 | [7 empty] | -90816.5285
-66150 | [7 empty] | -83287.3057
-56090 | [7 empty] | -70621.0881
-45780 | [7 empty] | -57640.1036
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-65190 | [7 empty] | -82078.601
-50140 | [7 empty] | -63129.6373
-58800 | [7 empty] | -74033.1606
-62350 | [7 empty] | -78502.8497
-66430 | [7 empty] | -83639.8446
-72920 | [7 empty] | -91811.1917
-75450 | [7 empty] | -94996.6321
-76540 | [7 empty] | -96369.0155
-74300 | [7 empty] | -93548.7047
-67790 | [7 empty] | -85352.1762
-60820 | [7 empty] | -76576.4767
-53970 | [7 empty] | -67951.8653
-46370 | [7 empty] | -58382.9534
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-82210 | [7 empty] | -103507.9275
-54080 | [7 empty] | -68090.3627
-57850 | [7 empty] | -72837.0466
-58200 | [7 empty] | -73277.7202
-50840 | [7 empty] | -64010.9845
-47020 | [7 empty] | -59201.3472
-40940 | [7 empty] | -51546.2176
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-52380 | [7 empty] | -65949.9482
-35190 | [7 empty] | -44306.5803
-45310 | [7 empty] | -57048.342
-55190 | [7 empty] | -69487.9275
-63980 | [7 empty] | -80555.1295
-73130 | [7 empty] | -92075.5959
-78350 | [7 empty] | -98647.9275
-82180 | [7 empty] | -103470.1554
-83930 | [7 empty] | -105673.5233
-83360 | [7 empty] | -104955.8549
-78440 | [7 empty] | -98761.2435
-68670 | [7 empty] | -86460.1554
-57320 | [7 empty] | -72169.7409
-45780 | [7 empty] | -57640.1036
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-48550 | [7 empty] | -61127.7202
-36010 | [7 empty] | -45339.0155
-49600 | [7 empty] | -62449.7409
-61990 | [7 empty] | -78049.5855
-71560 | [7 empty] | -90098.8601
-78030 | [7 empty] | -98245.0259
-83520 | [7 empty] | -105157.3057
-87930 | [7 empty] | -110709.7927
-89200 | [7 empty] | -112308.8083
-88180 | [7 empty] | -111024.5596
-83700 | [7 empty] | -105383.9378
-72300 | [7 empty] | -91030.5699
-59600 | [7 empty] | -75040.4145
-48140 | [7 empty] | -60611.5026
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-61850 | [7 empty] | -77873.3161
-39090 | [7 empty] | -49216.943
-43860 | [7 empty] | -55222.6943
-47710 | [7 empty] | -60070.1036
-49520 | [7 empty] | -62349.0155
-53250 | [7 empty] | -67045.3368
-51570 | [7 empty] | -64930.1036
-56600 | [7 empty] | -71263.2124
-67160 | [7 empty] | -84558.9637
-69500 | [7 empty] | -87505.1813
-63970 | [7 empty] | -80542.5389
-58010 | [7 empty] | -73038.4974
-50160 | [7 empty] | -63154.8187
-40540 | [7 empty] | -51042.5907
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-52110 | [7 empty] | -65610
-34490 | [7 empty] | -43425.2332
-45410 | [7 empty] | -57174.2487
-58750 | [7 empty] | -73970.2073
-69680 | [7 empty] | -87731.8135
-80560 | [7 empty] | -101430.4663
-86240 | [7 empty] | -108581.9689
-87590 | [7 empty] | -110281.7098
-89450 | [7 empty] | -112623.5751
-77510 | [7 empty] | -97590.3109
-70700 | [7 empty] | -89016.0622
-65880 | [7 empty] | -82947.3575
-56630 | [7 empty] | -71300.9845
-47520 | [7 empty] | -59830.8808
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-66220 | [7 empty] | -83375.4404
-44950 | [7 empty] | -56595.0777
-53720 | [7 empty] | -67637.0984
-59000 | [7 empty] | -74284.9741
-62500 | [7 empty] | -78691.7098
-64070 | [7 empty] | -80668.4456
-71950 | [7 empty] | -90589.8964
-80530 | [7 empty] | -101392.6943
-84190 | [7 empty] | -106000.8808
-85260 | [7 empty] | -107348.0829
-80850 | [7 empty] | -101795.5959
-71870 | [7 empty] | -90489.171
-62730 | [7 empty] | -78981.2953
-52380 | [7 empty] | -65949.9482
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-70960 | [7 empty] | -89343.4197
-46520 | [7 empty] | -58571.8135
-55400 | [7 empty] | -69752.3316
-62610 | [7 empty] | -78830.2073
-66130 | [7 empty] | -83262.1244
-69150 | [7 empty] | -87064.5078
-71510 | [7 empty] | -90035.9067
-70350 | [7 empty] | -88575.3886
-69310 | [7 empty] | -87265.9585
-66740 | [7 empty] | -84030.1554
-60900 | [7 empty] | -76677.2021
-53660 | [7 empty] | -67561.5544
-46290 | [7 empty] | -58282.228
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-103960 | [7 empty] | -130892.6425
-76840 | [7 empty] | -96746.7358
-76380 | [7 empty] | -96167.5648
-76020 | [7 empty] | -95714.3005
-72400 | [7 empty] | -91156.4767
-69350 | [7 empty] | -87316.3212
-68340 | [7 empty] | -86044.6632
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-70760 | [7 empty] | -89091.6062
-43260 | [7 empty] | -54467.2539
-52690 | [7 empty] | -66340.2591
-62110 | [7 empty] | -78200.6736
-69800 | [7 empty] | -87882.9016
-76310 | [7 empty] | -96079.4301
-80910 | [7 empty] | -101871.1399
-84590 | [7 empty] | -106504.5078
-85150 | [7 empty] | -107209.5855
-83450 | [7 empty] | -105069.171
-78350 | [7 empty] | -98647.9275
-69570 | [7 empty] | -87593.3161
-57900 | [7 empty] | -72900
-45260 | [7 empty] | -56985.3886
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-45310 | [7 empty] | -57048.342
-33680 | [7 empty] | -42405.3886
-45860 | [7 empty] | -57740.829
-58480 | [7 empty] | -73630.2591
-69010 | [7 empty] | -86888.2383
-76190 | [7 empty] | -95928.342
-81190 | [7 empty] | -102223.6788
-85800 | [7 empty] | -108027.9793
-87550 | [7 empty] | -110231.3472
-84860 | [7 empty] | -106844.456
-79890 | [7 empty] | -100586.8912
-71870 | [7 empty] | -90489.171
-60140 | [7 empty] | -75720.3109
-49210 | [7 empty] | -61958.7047
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-54400 | [7 empty] | -68493.2642
-39890 | [7 empty] | -50224.1969
-50750 | [7 empty] | -63897.6684
-61490 | [7 empty] | -77420.0518
-71340 | [7 empty] | -89821.8653
-79540 | [7 empty] | -100146.2176
-83560 | [7 empty] | -105207.6684
-88930 | [7 empty] | -111968.8601
-89490 | [7 empty] | -112673.9378
-87700 | [7 empty] | -110420.2073
-82150 | [7 empty] | -103432.3834
-73040 | [7 empty] | -91962.2798
-61570 | [7 empty] | -77520.7772
-49630 | [7 empty] | -62487.513
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-51880 | [7 empty] | -65320.4145
-36390 | [7 empty] | -45817.4611
-48780 | [7 empty] | -61417.3057
-60350 | [7 empty] | -75984.715
-69190 | [7 empty] | -87114.8705
-74320 | [7 empty] | -93573.886
-78450 | [7 empty] | -98773.8342
-83210 | [7 empty] | -104766.9948
-84250 | [7 empty] | -106076.4249
-81810 | [7 empty] | -103004.3005
-77790 | [7 empty] | -97942.8497
-68900 | [7 empty] | -86749.7409
-56860 | [7 empty] | -71590.5699
-44720 | [7 empty] | -56305.4922
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-48540 | [7 empty] | -61115.1295
-33630 | [7 empty] | -42342.4352
-45730 | [7 empty] | -57577.1503
-55040 | [7 empty] | -69299.0674
-61020 | [7 empty] | -76828.2902
-67360 | [7 empty] | -84810.7772
-65390 | [7 empty] | -82330.4145
-68370 | [7 empty] | -86082.4352
-64680 | [7 empty] | -81436.4767
-63260 | [7 empty] | -79648.601
-60760 | [7 empty] | -76500.9326
-51330 | [7 empty] | -64627.9275
-42220 | [7 empty] | -53157.8238
-34200 | [7 empty] | -43060.1036
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-49890 | [7 empty] | -62814.8705
-35010 | [7 empty] | -44079.9482
-41990 | [7 empty] | -52868.2383
-41960 | [7 empty] | -52830.4663
-50200 | [7 empty] | -63205.1813
-54530 | [7 empty] | -68656.943
-51220 | [7 empty] | -64489.4301
-48360 | [7 empty] | -60888.4974
-48300 | [7 empty] | -60812.9534
-51010 | [7 empty] | -64225.0259
-47800 | [7 empty] | -60183.4197
-40640 | [7 empty] | -51168.4974
-32800 | [7 empty] | -41297.4093
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-79460 | [7 empty] | -100045.4922
-62390 | [7 empty] | -78553.2124
-63400 | [7 empty] | -79824.8705
-67330 | [7 empty] | -84773.0052
-67750 | [7 empty] | -85301.8135
-64600 | [7 empty] | -81335.7513
-61120 | [7 empty] | -76954.1969
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-65890 | [7 empty] | -82959.9482
-46440 | [7 empty] | -58471.0881
-59660 | [7 empty] | -75115.9585
-72380 | [7 empty] | -91131.2953
-81440 | [7 empty] | -102538.4456
-87990 | [7 empty] | -110785.3368
-93270 | [7 empty] | -117433.2124
-97310 | [7 empty] | -122519.8446
-98700 | [7 empty] | -124269.9482
-97340 | [7 empty] | -122557.6166
-91770 | [7 empty] | -115544.6114
-82610 | [7 empty] | -104011.5544
-70940 | [7 empty] | -89318.2383
-58790 | [7 empty] | -74020.5699
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-78060 | [7 empty] | -98282.7979
-56390 | [7 empty] | -70998.8083
-68170 | [7 empty] | -85830.6218
-79720 | [7 empty] | -100372.8497
-88820 | [7 empty] | -111830.3627
-93940 | [7 empty] | -118276.7876
-97160 | [7 empty] | -122330.9845
-100120 | [7 empty] | -126057.8238
-102940 | [7 empty] | -129608.3938
-101460 | [7 empty] | -127744.9741
-96640 | [7 empty] | -121676.2694
-87550 | [7 empty] | -110231.3472
-75560 | [7 empty] | -95135.1295
-63340 | [7 empty] | -79749.3264
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-84010 | [7 empty] | -105774.2487
-53430 | [7 empty] | -67271.9689
-57990 | [7 empty] | -73013.3161
-62100 | [7 empty] | -78188.0829
-66330 | [7 empty] | -83513.9378
-67190 | [7 empty] | -84596.7358
-69570 | [7 empty] | -87593.3161
-70730 | [7 empty] | -89053.8342
-70820 | [7 empty] | -89167.1503
-74270 | [7 empty] | -93510.9326
-70860 | [7 empty] | -89217.513
-64740 | [7 empty] | -81512.0207
-54060 | [7 empty] | -68065.1813
-44800 | [7 empty] | -56406.2176
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-63630 | [7 empty] | -80114.456
-42120 | [7 empty] | -53031.9171
-48490 | [7 empty] | -61052.1762
-55510 | [7 empty] | -69890.829
-61390 | [7 empty] | -77294.1451
-64740 | [7 empty] | -81512.0207
-68750 | [7 empty] | -86560.8808
-70440 | [7 empty] | -88688.7047
-71530 | [7 empty] | -90061.0881
-72250 | [7 empty] | -90967.6166
-68230 | [7 empty] | -85906.1658
-62280 | [7 empty] | -78414.715
-54570 | [7 empty] | -68707.3057
-45030 | [7 empty] | -56695.8031
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-60890 | [7 empty] | -76664.6114
-43340 | [7 empty] | -54567.9793
-54690 | [7 empty] | -68858.3938
-65250 | [7 empty] | -82154.1451
-71250 | [7 empty] | -89708.5492
-76550 | [7 empty] | -96381.6062
-84390 | [7 empty] | -106252.6943
-87600 | [7 empty] | -110294.3005
-90670 | [7 empty] | -114159.6373
-92130 | [7 empty] | -115997.8756
-88850 | [7 empty] | -111868.1347
-79510 | [7 empty] | -100108.4456
-68510 | [7 empty] | -86258.7047
-56860 | [7 empty] | -71590.5699
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-80360 | [7 empty] | -101178.6528
-57910 | [7 empty] | -72912.5907
-63100 | [7 empty] | -79447.1503
-70170 | [7 empty] | -88348.7565
-73100 | [7 empty] | -92037.8238
-76460 | [7 empty] | -96268.2902
-82260 | [7 empty] | -103570.8808
-79480 | [7 empty] | -100070.6736
-77100 | [7 empty] | -97074.0933
-75320 | [7 empty] | -94832.9534
-68910 | [7 empty] | -86762.3316
-61430 | [7 empty] | -77344.5078
-53000 | [7 empty] | -66730.5699
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-97360 | [7 empty] | -122582.7979
-64770 | [7 empty] | -81549.7927
-54170 | [7 empty] | -68203.6788
-55480 | [7 empty] | -69853.057
-60030 | [7 empty] | -75581.8135
-57500 | [7 empty] | -72396.3731
-54170 | [7 empty] | -68203.6788
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-65600 | [7 empty] | -82594.8187
-37840 | [7 empty] | -47643.1088
-41600 | [7 empty] | -52377.2021
-45030 | [7 empty] | -56695.8031
-49510 | [7 empty] | -62336.4249
-53630 | [7 empty] | -67523.7824
-54440 | [7 empty] | -68543.6269
-56000 | [7 empty] | -70507.772
-55950 | [7 empty] | -70444.8187
-55580 | [7 empty] | -69978.9637
-52710 | [7 empty] | -66365.4404
-46860 | [7 empty] | -58999.8964
-39650 | [7 empty] | -49922.0207
-32180 | [7 empty] | -40516.7876
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-43740 | [7 empty] | -55071.6062
-27980 | [7 empty] | -35228.7047
-35100 | [7 empty] | -44193.2642
-48030 | [7 empty] | -60473.0052
-54820 | [7 empty] | -69022.0725
-61550 | [7 empty] | -77495.5959
-66730 | [7 empty] | -84017.5648
-73410 | [7 empty] | -92428.1347
-71870 | [7 empty] | -90489.171
-65320 | [7 empty] | -82242.2798
-61880 | [7 empty] | -77911.0881
-54600 | [7 empty] | -68745.0777
-45940 | [7 empty] | -57841.5544
-37880 | [7 empty] | -47693.4715
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-46750 | [7 empty] | -58861.399
-30680 | [7 empty] | -38628.1865
-44030 | [7 empty] | -55436.7358
-55200 | [7 empty] | -69500.5181
-60810 | [7 empty] | -76563.886
-62150 | [7 empty] | -78251.0363
-69870 | [7 empty] | -87971.0363
-73790 | [7 empty] | -92906.5803
-80790 | [7 empty] | -101720.0518
-79180 | [7 empty] | -99692.9534
-72860 | [7 empty] | -91735.6477
-64640 | [7 empty] | -81386.114
-55930 | [7 empty] | -70419.6373
-45750 | [7 empty] | -57602.3316
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-54170 | [7 empty] | -68203.6788
-36740 | [7 empty] | -46258.1347
-48310 | [7 empty] | -60825.544
-60430 | [7 empty] | -76085.4404
-70410 | [7 empty] | -88650.9326
-76820 | [7 empty] | -96721.5544
-81770 | [7 empty] | -102953.9378
-83630 | [7 empty] | -105295.8031
-87000 | [7 empty] | -109538.8601
-86350 | [7 empty] | -108720.4663
-81890 | [7 empty] | -103105.0259
-73620 | [7 empty] | -92692.5389
-62940 | [7 empty] | -79245.6995
-51830 | [7 empty] | -65257.4611
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-61300 | [7 empty] | -77180.829
-44010 | [7 empty] | -55411.5544
-56240 | [7 empty] | -70809.9482
-67350 | [7 empty] | -84798.1865
-73430 | [7 empty] | -92453.3161
-79130 | [7 empty] | -99630
-82930 | [7 empty] | -104414.456
-83910 | [7 empty] | -105648.342
-85480 | [7 empty] | -107625.0777
-85080 | [7 empty] | -107121.4508
-80590 | [7 empty] | -101468.2383
-69260 | [7 empty] | -87203.0052
-59140 | [7 empty] | -74461.2435
-49090 | [7 empty] | -61807.6166
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-70100 | [7 empty] | -88260.6218
-49620 | [7 empty] | -62474.9223
-56520 | [7 empty] | -71162.487
-63580 | [7 empty] | -80051.5026
-69520 | [7 empty] | -87530.3627
-73660 | [7 empty] | -92742.9016
-76760 | [7 empty] | -96646.0104
-78460 | [7 empty] | -98786.4249
-75060 | [7 empty] | -94505.5959
-70840 | [7 empty] | -89192.3316
-64220 | [7 empty] | -80857.3057
-54740 | [7 empty] | -68921.3472
-45330 | [7 empty] | -57073.5233
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-103550 | [7 empty] | -130376.4249
-79500 | [7 empty] | -100095.8549
-81820 | [7 empty] | -103016.8912
-83050 | [7 empty] | -104565.544
-82950 | [7 empty] | -104439.6373
-80720 | [7 empty] | -101631.9171
-75070 | [7 empty] | -94518.1865
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-95370 | [7 empty] | -120077.2539
-65820 | [7 empty] | -82871.8135
-75050 | [7 empty] | -94493.0052
-85340 | [7 empty] | -107448.8083
-93420 | [7 empty] | -117622.0725
-99930 | [7 empty] | -125818.601
-103740 | [7 empty] | -130615.6477
-110330 | [7 empty] | -138912.9016
-110720 | [7 empty] | -139403.9378
-108110 | [7 empty] | -136117.772
-102350 | [7 empty] | -128865.544
-93060 | [7 empty] | -117168.8083
-80650 | [7 empty] | -101543.7824
-68420 | [7 empty] | -86145.3886
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-93260 | [7 empty] | -117420.6218
-64760 | [7 empty] | -81537.2021
-73620 | [7 empty] | -92692.5389
-84360 | [7 empty] | -106214.9223
-91820 | [7 empty] | -115607.5648
-98920 | [7 empty] | -124546.943
-105010 | [7 empty] | -132214.6632
-109380 | [7 empty] | -137716.7876
-110980 | [7 empty] | -139731.2953
-109160 | [7 empty] | -137439.7927
-104020 | [7 empty] | -130968.1865
-95120 | [7 empty] | -119762.487
-82970 | [7 empty] | -104464.8187
-69010 | [7 empty] | -86888.2383
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-91190 | [7 empty] | -114814.3523
-62430 | [7 empty] | -78603.5751
-72160 | [7 empty] | -90854.3005
-82360 | [7 empty] | -103696.7876
-91280 | [7 empty] | -114927.6684
-98270 | [7 empty] | -123728.5492
-100520 | [7 empty] | -126561.4508
-105540 | [7 empty] | -132881.9689
-92410 | [7 empty] | -116350.4145
-77590 | [7 empty] | -97691.0363
-67320 | [7 empty] | -84760.4145
-59230 | [7 empty] | -74574.5596
-50180 | [7 empty] | -63180
-42910 | [7 empty] | -54026.5803
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-57190 | [7 empty] | -72006.0622
-38290 | [7 empty] | -48209.6891
-50830 | [7 empty] | -63998.3938
-61880 | [7 empty] | -77911.0881
-69730 | [7 empty] | -87794.7668
-75610 | [7 empty] | -95198.0829
-76250 | [7 empty] | -96003.886
-82830 | [7 empty] | -104288.5492
-82880 | [7 empty] | -104351.5026
-81400 | [7 empty] | -102488.0829
-77690 | [7 empty] | -97816.943
-69380 | [7 empty] | -87354.0933
-56900 | [7 empty] | -71640.9326
-44690 | [7 empty] | -56267.7202
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-39740 | [7 empty] | -50035.3368
-27000 | [7 empty] | -33994.8187
-40070 | [7 empty] | -50450.829
-52590 | [7 empty] | -66214.3523
-62910 | [7 empty] | -79207.9275
-69680 | [7 empty] | -87731.8135
-75950 | [7 empty] | -95626.1658
-79250 | [7 empty] | -99781.0881
-82540 | [7 empty] | -103923.4197
-80470 | [7 empty] | -101317.1503
-75070 | [7 empty] | -94518.1865
-66460 | [7 empty] | -83677.6166
-57080 | [7 empty] | -71867.5648
-45390 | [7 empty] | -57149.0674
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-54680 | [7 empty] | -68845.8031
-44040 | [7 empty] | -55449.3264
-52660 | [7 empty] | -66302.487
-60180 | [7 empty] | -75770.6736
-64280 | [7 empty] | -80932.8497
-65380 | [7 empty] | -82317.8238
-63300 | [7 empty] | -79698.9637
-69040 | [7 empty] | -86926.0104
-68520 | [7 empty] | -86271.2953
-65560 | [7 empty] | -82544.456
-61290 | [7 empty] | -77168.2383
-53130 | [7 empty] | -66894.2487
-44700 | [7 empty] | -56280.3109
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-100280 | [7 empty] | -126259.2746
-75460 | [7 empty] | -95009.2228
-71540 | [7 empty] | -90073.6788
-64880 | [7 empty] | -81688.2902
-60010 | [7 empty] | -75556.6321
-53940 | [7 empty] | -67914.0933
-53360 | [7 empty] | -67183.8342
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-64660 | [7 empty] | -81411.2953
-43270 | [7 empty] | -54479.8446
-50440 | [7 empty] | -63507.3575
-59900 | [7 empty] | -75418.1347
-68790 | [7 empty] | -86611.2435
-76110 | [7 empty] | -95827.6166
-82730 | [7 empty] | -104162.6425
-88480 | [7 empty] | -111402.2798
-90010 | [7 empty] | -113328.6528
-88800 | [7 empty] | -111805.1813
-76070 | [7 empty] | -95777.2539
-65720 | [7 empty] | -82745.9067
-56100 | [7 empty] | -70633.6788
-47670 | [7 empty] | -60019.7409
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-65990 | [7 empty] | -83085.8549
-45230 | [7 empty] | -56947.6166
-56240 | [7 empty] | -70809.9482
-67760 | [7 empty] | -85314.4041
-77660 | [7 empty] | -97779.171
-85100 | [7 empty] | -107146.6321
-88640 | [7 empty] | -111603.7306
-93770 | [7 empty] | -118062.7461
-92290 | [7 empty] | -116199.3264
-90080 | [7 empty] | -113416.7876
-84610 | [7 empty] | -106529.6891
-76310 | [7 empty] | -96079.4301
-66060 | [7 empty] | -83173.9896
-53760 | [7 empty] | -67687.4611
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-59010 | [7 empty] | -74297.5648
-42710 | [7 empty] | -53774.7668
-56280 | [7 empty] | -70860.3109
-68390 | [7 empty] | -86107.6166
-76470 | [7 empty] | -96280.8808
-83180 | [7 empty] | -104729.2228
-87930 | [7 empty] | -110709.7927
-93470 | [7 empty] | -117685.0259
-96030 | [7 empty] | -120908.2383
-95910 | [7 empty] | -120757.1503
-89990 | [7 empty] | -113303.4715
-80690 | [7 empty] | -101594.1451
-69460 | [7 empty] | -87454.8187
-58210 | [7 empty] | -73290.3109
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-64060 | [7 empty] | -80655.8549
-44670 | [7 empty] | -56242.5389
-56950 | [7 empty] | -71703.886
-69660 | [7 empty] | -87706.6321
-80020 | [7 empty] | -100750.5699
-86530 | [7 empty] | -108947.0984
-90610 | [7 empty] | -114084.0933
-95000 | [7 empty] | -119611.399
-96280 | [7 empty] | -121223.0052
-94910 | [7 empty] | -119498.0829
-91440 | [7 empty] | -115129.1192
-82650 | [7 empty] | -104061.9171
-70560 | [7 empty] | -88839.7927
-58180 | [7 empty] | -73252.5389
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-72380 | [7 empty] | -91131.2953
-50360 | [7 empty] | -63406.6321
-61730 | [7 empty] | -77722.228
-73320 | [7 empty] | -92314.8187
-82550 | [7 empty] | -103936.0104
-85570 | [7 empty] | -107738.3938
-85120 | [7 empty] | -107171.8135
-87840 | [7 empty] | -110596.4767
-91950 | [7 empty] | -115771.2435
-89940 | [7 empty] | -113240.5181
-80970 | [7 empty] | -101946.6839
-67260 | [7 empty] | -84684.8705
-57310 | [7 empty] | -72157.1503
-48150 | [7 empty] | -60624.0933
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-71260 | [7 empty] | -89721.1399
-52690 | [7 empty] | -66340.2591
-58420 | [7 empty] | -73554.715
-65840 | [7 empty] | -82896.9948
-72620 | [7 empty] | -91433.4715
-72910 | [7 empty] | -91798.601
-59250 | [7 empty] | -74599.7409
-50420 | [7 empty] | -63482.1762
-49390 | [7 empty] | -62185.3368
-47430 | [7 empty] | -59717.5648
-45260 | [7 empty] | -56985.3886
-40320 | [7 empty] | -50765.5959
-34310 | [7 empty] | -43198.601
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-99080 | [7 empty] | -124748.3938
-75090 | [7 empty] | -94543.3679
-64940 | [7 empty] | -81763.8342
-60440 | [7 empty] | -76098.0311
-51660 | [7 empty] | -65043.4197
-45740 | [7 empty] | -57589.7409
-49300 | [7 empty] | -62072.0207
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-69040 | [7 empty] | -86926.0104
-48810 | [7 empty] | -61455.0777
-59820 | [7 empty] | -75317.4093
-70510 | [7 empty] | -88776.8394
-77620 | [7 empty] | -97728.8083
-86130 | [7 empty] | -108443.4715
-87820 | [7 empty] | -110571.2953
-91450 | [7 empty] | -115141.7098
-81680 | [7 empty] | -102840.6218
-77630 | [7 empty] | -97741.399
-72910 | [7 empty] | -91798.601
-64960 | [7 empty] | -81789.0155
-55580 | [7 empty] | -69978.9637
-46740 | [7 empty] | -58848.8083
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-56090 | [7 empty] | -70621.0881
-39300 | [7 empty] | -49481.3472
-52490 | [7 empty] | -66088.4456
-64150 | [7 empty] | -80769.171
-71360 | [7 empty] | -89847.0466
-80150 | [7 empty] | -100914.2487
-86770 | [7 empty] | -109249.2746
-91970 | [7 empty] | -115796.4249
-94470 | [7 empty] | -118944.0933
-92770 | [7 empty] | -116803.6788
-88440 | [7 empty] | -111351.9171
-79090 | [7 empty] | -99579.6373
-67400 | [7 empty] | -84861.1399
-55700 | [7 empty] | -70130.0518
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-63020 | [7 empty] | -79346.4249
-44240 | [7 empty] | -55701.1399
-55710 | [7 empty] | -70142.6425
-67570 | [7 empty] | -85075.1813
-77740 | [7 empty] | -97879.8964
-86140 | [7 empty] | -108456.0622
-91000 | [7 empty] | -114575.1295
-95170 | [7 empty] | -119825.4404
-94520 | [7 empty] | -119007.0466
-93900 | [7 empty] | -118226.4249
-87490 | [7 empty] | -110155.8031
-80750 | [7 empty] | -101669.6891
-69560 | [7 empty] | -87580.7254
-57800 | [7 empty] | -72774.0933
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-67640 | [7 empty] | -85163.3161
-45070 | [7 empty] | -56746.1658
-55670 | [7 empty] | -70092.2798
-67300 | [7 empty] | -84735.2332
-76890 | [7 empty] | -96809.6891
-84330 | [7 empty] | -106177.1503
-90380 | [7 empty] | -113794.5078
-95910 | [7 empty] | -120757.1503
-96590 | [7 empty] | -121613.3161
-92150 | [7 empty] | -116023.057
-80520 | [7 empty] | -101380.1036
-65170 | [7 empty] | -82053.4197
-56430 | [7 empty] | -71049.171
-48590 | [7 empty] | -61178.0829
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-64190 | [7 empty] | -80819.5337
-44540 | [7 empty] | -56078.8601
-54030 | [7 empty] | -68027.4093
-58790 | [7 empty] | -74020.5699
-59700 | [7 empty] | -75166.3212
-59390 | [7 empty] | -74776.0104
-63420 | [7 empty] | -79850.0518
-68170 | [7 empty] | -85830.6218
-78940 | [7 empty] | -99390.7772
-78530 | [7 empty] | -98874.5596
-76330 | [7 empty] | -96104.6114
-70650 | [7 empty] | -88953.1088
-60930 | [7 empty] | -76714.9741
-49970 | [7 empty] | -62915.5959
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-62660 | [7 empty] | -78893.1606
-38710 | [7 empty] | -48738.4974
-37980 | [7 empty] | -47819.3782
-40450 | [7 empty] | -50929.2746
-43770 | [7 empty] | -55109.3782
-43400 | [7 empty] | -54643.5233
-46110 | [7 empty] | -58055.5959
-46040 | [7 empty] | -57967.4611
-44670 | [7 empty] | -56242.5389
-42870 | [7 empty] | -53976.2176
-37860 | [7 empty] | -47668.2902
-33110 | [7 empty] | -41687.7202
-28500 | [7 empty] | -35883.4197
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-55760 | [7 empty] | -70205.5959
-34090 | [7 empty] | -42921.6062
-33260 | [7 empty] | -41876.5803
-32360 | [7 empty] | -40743.4197
-30150 | [7 empty] | -37960.8808
-28290 | [7 empty] | -35619.0155
-27020 | [7 empty] | -34020
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-50780 | [7 empty] | -63935.4404
-35860 | [7 empty] | -45150.1554
-43790 | [7 empty] | -55134.5596
-50790 | [7 empty] | -63948.0311
-64460 | [7 empty] | -81159.4819
-74720 | [7 empty] | -94077.513
-81990 | [7 empty] | -103230.9326
-86800 | [7 empty] | -109287.0466
-83900 | [7 empty] | -105635.7513
-83790 | [7 empty] | -105497.2539
-73530 | [7 empty] | -92579.2228
-64680 | [7 empty] | -81436.4767
-54190 | [7 empty] | -68228.8601
-44520 | [7 empty] | -56053.6788
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-61270 | [7 empty] | -77143.057
-41150 | [7 empty] | -51810.6218
-47870 | [7 empty] | -60271.5544
-55590 | [7 empty] | -69991.5544
-63020 | [7 empty] | -79346.4249
-72320 | [7 empty] | -91055.7513
-80470 | [7 empty] | -101317.1503
-82310 | [7 empty] | -103633.8342
-83050 | [7 empty] | -104565.544
-81490 | [7 empty] | -102601.399
-74760 | [7 empty] | -94127.8756
-67480 | [7 empty] | -84961.8653
-56320 | [7 empty] | -70910.6736
-45310 | [7 empty] | -57048.342
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-63620 | [7 empty] | -80101.8653
-40440 | [7 empty] | -50916.6839
-52950 | [7 empty] | -66667.6166
-64500 | [7 empty] | -81209.8446
-73440 | [7 empty] | -92465.9067
-80270 | [7 empty] | -101065.3368
-85470 | [7 empty] | -107612.487
-83580 | [7 empty] | -105232.8497
-84810 | [7 empty] | -106781.5026
-83040 | [7 empty] | -104552.9534
-76880 | [7 empty] | -96797.0984
-68290 | [7 empty] | -85981.7098
-57330 | [7 empty] | -72182.3316
-46970 | [7 empty] | -59138.3938
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-66430 | [7 empty] | -83639.8446
-46360 | [7 empty] | -58370.3627
-57320 | [7 empty] | -72169.7409
-69530 | [7 empty] | -87542.9534
-79300 | [7 empty] | -99844.0415
-87150 | [7 empty] | -109727.7202
-89200 | [7 empty] | -112308.8083
-88100 | [7 empty] | -110923.8342
-84540 | [7 empty] | -106441.5544
-87000 | [7 empty] | -109538.8601
-75950 | [7 empty] | -95626.1658
-63560 | [7 empty] | -80026.3212
-53570 | [7 empty] | -67448.2383
-46650 | [7 empty] | -58735.4922
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-64010 | [7 empty] | -80592.9016
-45110 | [7 empty] | -56796.5285
-56820 | [7 empty] | -71540.2073
-68530 | [7 empty] | -86283.886
-74840 | [7 empty] | -94228.601
-83820 | [7 empty] | -105535.0259
-92610 | [7 empty] | -116602.228
-92410 | [7 empty] | -116350.4145
-97070 | [7 empty] | -122217.6684
-95690 | [7 empty] | -120480.1554
-89010 | [7 empty] | -112069.5855
-80480 | [7 empty] | -101329.7409
-69750 | [7 empty] | -87819.9482
-57490 | [7 empty] | -72383.7824
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-81820 | [7 empty] | -103016.8912
-58750 | [7 empty] | -73970.2073
-64360 | [7 empty] | -81033.5751
-70660 | [7 empty] | -88965.6995
-76700 | [7 empty] | -96570.4663
-80340 | [7 empty] | -101153.4715
-83470 | [7 empty] | -105094.3523
-71890 | [7 empty] | -90514.3523
-62220 | [7 empty] | -78339.171
-51870 | [7 empty] | -65307.8238
-46180 | [7 empty] | -58143.7306
-41420 | [7 empty] | -52150.5699
-39200 | [7 empty] | -49355.4404
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-106990 | [7 empty] | -134707.6166
-79100 | [7 empty] | -99592.228
-80560 | [7 empty] | -101430.4663
-77990 | [7 empty] | -98194.6632
-81310 | [7 empty] | -102374.7668
-67520 | [7 empty] | -85012.228
-56270 | [7 empty] | -70847.7202
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-75800 | [7 empty] | -95437.3057
-49470 | [7 empty] | -62286.0622
-60380 | [7 empty] | -76022.487
-72340 | [7 empty] | -91080.9326
-81110 | [7 empty] | -102122.9534
-87830 | [7 empty] | -110583.886
-93050 | [7 empty] | -117156.2176
-97910 | [7 empty] | -123275.285
-99260 | [7 empty] | -124975.0259
-97440 | [7 empty] | -122683.5233
-93090 | [7 empty] | -117206.5803
-83050 | [7 empty] | -104565.544
-70810 | [7 empty] | -89154.5596
-58700 | [7 empty] | -73907.2539
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-78540 | [7 empty] | -98887.1503
-53630 | [7 empty] | -67523.7824
-63700 | [7 empty] | -80202.5907
-73970 | [7 empty] | -93133.2124
-83190 | [7 empty] | -104741.8135
-88590 | [7 empty] | -111540.7772
-80430 | [7 empty] | -101266.7876
-79620 | [7 empty] | -100246.943
-86640 | [7 empty] | -109085.5959
-83020 | [7 empty] | -104527.772
-80870 | [7 empty] | -101820.7772
-70130 | [7 empty] | -88298.3938
-58680 | [7 empty] | -73882.0725
-47120 | [7 empty] | -59327.2539
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-60260 | [7 empty] | -75871.399
-39180 | [7 empty] | -49330.2591
-52390 | [7 empty] | -65962.5389
-63600 | [7 empty] | -80076.6839
-71580 | [7 empty] | -90124.0415
-76360 | [7 empty] | -96142.3834
-73720 | [7 empty] | -92818.4456
-68610 | [7 empty] | -86384.6114
-74250 | [7 empty] | -93485.7513
-73420 | [7 empty] | -92440.7254
-71020 | [7 empty] | -89418.9637
-64440 | [7 empty] | -81134.3005
-54680 | [7 empty] | -68845.8031
-43770 | [7 empty] | -55109.3782
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-49120 | [7 empty] | -61845.3886
-31490 | [7 empty] | -39648.0311
-45580 | [7 empty] | -57388.2902
-59160 | [7 empty] | -74486.4249
-67270 | [7 empty] | -84697.4611
-74730 | [7 empty] | -94090.1036
-79950 | [7 empty] | -100662.4352
-84560 | [7 empty] | -106466.7358
-85710 | [7 empty] | -107914.6632
-84640 | [7 empty] | -106567.4611
-79550 | [7 empty] | -100158.8083
-71140 | [7 empty] | -89570.0518
-59600 | [7 empty] | -75040.4145
-47780 | [7 empty] | -60158.2383
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-51140 | [7 empty] | -64388.7047
-35640 | [7 empty] | -44873.1606
-49580 | [7 empty] | -62424.5596
-62910 | [7 empty] | -79207.9275
-73780 | [7 empty] | -92893.9896
-80150 | [7 empty] | -100914.2487
-85750 | [7 empty] | -107965.0259
-89030 | [7 empty] | -112094.7668
-90920 | [7 empty] | -114474.4041
-81510 | [7 empty] | -102626.5803
-79220 | [7 empty] | -99743.3161
-70070 | [7 empty] | -88222.8497
-59680 | [7 empty] | -75141.1399
-48490 | [7 empty] | -61052.1762
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-68670 | [7 empty] | -86460.1554
-50840 | [7 empty] | -64010.9845
-57560 | [7 empty] | -72471.9171
-65070 | [7 empty] | -81927.513
-69460 | [7 empty] | -87454.8187
-72800 | [7 empty] | -91660.1036
-76120 | [7 empty] | -95840.2073
-78860 | [7 empty] | -99290.0518
-71600 | [7 empty] | -90149.2228
-69200 | [7 empty] | -87127.4611
-59680 | [7 empty] | -75141.1399
-51380 | [7 empty] | -64690.8808
-44460 | [7 empty] | -55978.1347
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-74090 | [7 empty] | -93284.3005
-43880 | [7 empty] | -55247.8756
-44480 | [7 empty] | -56003.3161
-46820 | [7 empty] | -58949.5337
-47630 | [7 empty] | -59969.3782
-47140 | [7 empty] | -59352.4352
-50090 | [7 empty] | -63066.6839
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-59800 | [7 empty] | -75292.228
-39250 | [7 empty] | -49418.3938
-50620 | [7 empty] | -63733.9896
-61900 | [7 empty] | -77936.2694
-68640 | [7 empty] | -86422.3834
-75340 | [7 empty] | -94858.1347
-81240 | [7 empty] | -102286.6321
-86010 | [7 empty] | -108292.3834
-83180 | [7 empty] | -104729.2228
-83810 | [7 empty] | -105522.4352
-79760 | [7 empty] | -100423.2124
-70880 | [7 empty] | -89242.6943
-58310 | [7 empty] | -73416.2176
-47020 | [7 empty] | -59201.3472
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-59540 | [7 empty] | -74964.8705
-36990 | [7 empty] | -46572.9016
-43900 | [7 empty] | -55273.057
-49100 | [7 empty] | -61820.2073
-54840 | [7 empty] | -69047.2539
-59170 | [7 empty] | -74499.0155
-70960 | [7 empty] | -89343.4197
-76480 | [7 empty] | -96293.4715
-80390 | [7 empty] | -101216.4249
-78030 | [7 empty] | -98245.0259
-72380 | [7 empty] | -91131.2953
-65110 | [7 empty] | -81977.8756
-56140 | [7 empty] | -70684.0415
-43330 | [7 empty] | -54555.3886
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-53960 | [7 empty] | -67939.2746
-35020 | [7 empty] | -44092.5389
-40990 | [7 empty] | -51609.171
-47640 | [7 empty] | -59981.9689
-52420 | [7 empty] | -66000.3109
-62110 | [7 empty] | -78200.6736
-68520 | [7 empty] | -86271.2953
-70800 | [7 empty] | -89141.9689
-73060 | [7 empty] | -91987.4611
-68790 | [7 empty] | -86611.2435
-62260 | [7 empty] | -78389.5337
-50570 | [7 empty] | -63671.0363
-40720 | [7 empty] | -51269.2228
-33770 | [7 empty] | -42518.7047
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-48250 | [7 empty] | -60750
-31260 | [7 empty] | -39358.4456
-39350 | [7 empty] | -49544.3005
-47470 | [7 empty] | -59767.9275
-57750 | [7 empty] | -72711.1399
-67850 | [7 empty] | -85427.7202
-73750 | [7 empty] | -92856.2176
-72690 | [7 empty] | -91521.6062
-77030 | [7 empty] | -96985.9585
-78500 | [7 empty] | -98836.7876
-75140 | [7 empty] | -94606.3212
-68170 | [7 empty] | -85830.6218
-57200 | [7 empty] | -72018.6528
-46570 | [7 empty] | -58634.7668
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-56960 | [7 empty] | -71716.4767
-36060 | [7 empty] | -45401.9689
-46160 | [7 empty] | -58118.5492
-59160 | [7 empty] | -74486.4249
-69440 | [7 empty] | -87429.6373
-72830 | [7 empty] | -91697.8756
-82300 | [7 empty] | -103621.2435
-84220 | [7 empty] | -106038.6528
-87150 | [7 empty] | -109727.7202
-86370 | [7 empty] | -108745.6477
-77140 | [7 empty] | -97124.456
-67260 | [7 empty] | -84684.8705
-57020 | [7 empty] | -71792.0207
-46650 | [7 empty] | -58735.4922
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-58420 | [7 empty] | -73554.715
-42850 | [7 empty] | -53951.0363
-49330 | [7 empty] | -62109.7927
-55290 | [7 empty] | -69613.8342
-62040 | [7 empty] | -78112.5389
-63970 | [7 empty] | -80542.5389
-63110 | [7 empty] | -79459.7409
-61120 | [7 empty] | -76954.1969
-57270 | [7 empty] | -72106.7876
-51890 | [7 empty] | -65333.0052
-47180 | [7 empty] | -59402.7979
-42840 | [7 empty] | -53938.4456
-36370 | [7 empty] | -45792.2798
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-87010 | [7 empty] | -109551.4508
-65790 | [7 empty] | -82834.0415
-63450 | [7 empty] | -79887.8238
-66320 | [7 empty] | -83501.3472
-66830 | [7 empty] | -84143.4715
-60680 | [7 empty] | -76400.2073
-57540 | [7 empty] | -72446.7358
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-65040 | [7 empty] | -81889.7409
-40920 | [7 empty] | -51521.0363
-46680 | [7 empty] | -58773.2642
-52390 | [7 empty] | -65962.5389
-62890 | [7 empty] | -79182.7461
-71610 | [7 empty] | -90161.8135
-77730 | [7 empty] | -97867.3057
-84260 | [7 empty] | -106089.0155
-81670 | [7 empty] | -102828.0311
-77820 | [7 empty] | -97980.6218
-70010 | [7 empty] | -88147.3057
-60610 | [7 empty] | -76312.0725
-51370 | [7 empty] | -64678.2902
-43210 | [7 empty] | -54404.3005
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-59490 | [7 empty] | -74901.9171
-42050 | [7 empty] | -52943.7824
-55120 | [7 empty] | -69399.7927
-67040 | [7 empty] | -84407.8756
-74350 | [7 empty] | -93611.658
-80050 | [7 empty] | -100788.342
-83820 | [7 empty] | -105535.0259
-88580 | [7 empty] | -111528.1865
-90960 | [7 empty] | -114524.7668
-90050 | [7 empty] | -113379.0155
-85260 | [7 empty] | -107348.0829
-76830 | [7 empty] | -96734.1451
-66090 | [7 empty] | -83211.7617
-54000 | [7 empty] | -67989.6373
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-71210 | [7 empty] | -89658.1865
-49740 | [7 empty] | -62626.0104
-61390 | [7 empty] | -77294.1451
-70760 | [7 empty] | -89091.6062
-80970 | [7 empty] | -101946.6839
-84750 | [7 empty] | -106705.9585
-88930 | [7 empty] | -111968.8601
-90120 | [7 empty] | -113467.1503
-74510 | [7 empty] | -93813.1088
-70350 | [7 empty] | -88575.3886
-63720 | [7 empty] | -80227.772
-55360 | [7 empty] | -69701.9689
-47280 | [7 empty] | -59528.7047
-39760 | [7 empty] | -50060.5181
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-58930 | [7 empty] | -74196.8394
-41950 | [7 empty] | -52817.8756
-55240 | [7 empty] | -69550.8808
-68870 | [7 empty] | -86711.9689
-78910 | [7 empty] | -99353.0052
-86670 | [7 empty] | -109123.3679
-92630 | [7 empty] | -116627.4093
-94060 | [7 empty] | -118427.8756
-83800 | [7 empty] | -105509.8446
-75260 | [7 empty] | -94757.4093
-69610 | [7 empty] | -87643.6788
-63020 | [7 empty] | -79346.4249
-56620 | [7 empty] | -71288.3938
-48110 | [7 empty] | -60573.7306
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-65850 | [7 empty] | -82909.5855
-46300 | [7 empty] | -58294.8187
-58240 | [7 empty] | -73328.0829
-70550 | [7 empty] | -88827.2021
-80330 | [7 empty] | -101140.8808
-87200 | [7 empty] | -109790.6736
-93310 | [7 empty] | -117483.5751
-97180 | [7 empty] | -122356.1658
-97920 | [7 empty] | -123287.8756
-97370 | [7 empty] | -122595.3886
-87610 | [7 empty] | -110306.8912
-76710 | [7 empty] | -96583.057
-65830 | [7 empty] | -82884.4041
-55390 | [7 empty] | -69739.7409
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-78650 | [7 empty] | -99025.6477
-56260 | [7 empty] | -70835.1295
-62370 | [7 empty] | -78528.0311
-68610 | [7 empty] | -86384.6114
-73940 | [7 empty] | -93095.4404
-78860 | [7 empty] | -99290.0518
-83460 | [7 empty] | -105081.7617
-81370 | [7 empty] | -102450.3109
-79160 | [7 empty] | -99667.772
-74310 | [7 empty] | -93561.2953
-65230 | [7 empty] | -82128.9637
-56420 | [7 empty] | -71036.5803
-49220 | [7 empty] | -61971.2953
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-104650 | [7 empty] | -131761.399
-72760 | [7 empty] | -91609.7409
-76070 | [7 empty] | -95777.2539
-76130 | [7 empty] | -95852.7979
-76040 | [7 empty] | -95739.4819
-74810 | [7 empty] | -94190.829
-72230 | [7 empty] | -90942.4352
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-80350 | [7 empty] | -101166.0622
-51800 | [7 empty] | -65219.6891
-60060 | [7 empty] | -75619.5855
-71790 | [7 empty] | -90388.4456
-81840 | [7 empty] | -103042.0725
-85970 | [7 empty] | -108242.0207
-85140 | [7 empty] | -107196.9948
-76170 | [7 empty] | -95903.1606
-72870 | [7 empty] | -91748.2383
-76810 | [7 empty] | -96708.9637
-75570 | [7 empty] | -95147.7202
-69720 | [7 empty] | -87782.1762
-59620 | [7 empty] | -75065.5959
-49880 | [7 empty] | -62802.2798
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-67080 | [7 empty] | -84458.2383
-44630 | [7 empty] | -56192.1762
-55930 | [7 empty] | -70419.6373
-66680 | [7 empty] | -83954.6114
-74060 | [7 empty] | -93246.5285
-79960 | [7 empty] | -100675.0259
-83110 | [7 empty] | -104641.0881
-80640 | [7 empty] | -101531.1917
-82620 | [7 empty] | -104024.1451
-80070 | [7 empty] | -100813.5233
-75790 | [7 empty] | -95424.715
-67850 | [7 empty] | -85427.7202
-55520 | [7 empty] | -69903.4197
-44610 | [7 empty] | -56166.9948
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-62310 | [7 empty] | -78452.487
-41260 | [7 empty] | -51949.1192
-51740 | [7 empty] | -65144.1451
-62440 | [7 empty] | -78616.1658
-67790 | [7 empty] | -85352.1762
-77010 | [7 empty] | -96960.7772
-81850 | [7 empty] | -103054.6632
-85720 | [7 empty] | -107927.2539
-85100 | [7 empty] | -107146.6321
-85650 | [7 empty] | -107839.1192
-81220 | [7 empty] | -102261.4508
-72120 | [7 empty] | -90803.9378
-60550 | [7 empty] | -76236.5285
-50320 | [7 empty] | -63356.2694
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-66220 | [7 empty] | -83375.4404
-46010 | [7 empty] | -57929.6891
-57300 | [7 empty] | -72144.5596
-67980 | [7 empty] | -85591.399
-76580 | [7 empty] | -96419.3782
-76580 | [7 empty] | -96419.3782
-85570 | [7 empty] | -107738.3938
-87380 | [7 empty] | -110017.3057
-89690 | [7 empty] | -112925.7513
-83630 | [7 empty] | -105295.8031
-70140 | [7 empty] | -88310.9845
-57760 | [7 empty] | -72723.7306
-47720 | [7 empty] | -60082.6943
-39730 | [7 empty] | -50022.7461
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-55440 | [7 empty] | -69802.6943
-36820 | [7 empty] | -46358.8601
-48490 | [7 empty] | -61052.1762
-59460 | [7 empty] | -74864.1451
-69650 | [7 empty] | -87694.0415
-73790 | [7 empty] | -92906.5803
-78270 | [7 empty] | -98547.2021
-79130 | [7 empty] | -99630
-80820 | [7 empty] | -101757.8238
-83840 | [7 empty] | -105560.2073
-78960 | [7 empty] | -99415.9585
-70760 | [7 empty] | -89091.6062
-59610 | [7 empty] | -75053.0052
-49170 | [7 empty] | -61908.342
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-68280 | [7 empty] | -85969.1192
-49380 | [7 empty] | -62172.7461
-56410 | [7 empty] | -71023.9896
-62330 | [7 empty] | -78477.6684
-66210 | [7 empty] | -83362.8497
-67690 | [7 empty] | -85226.2694
-72250 | [7 empty] | -90967.6166
-72510 | [7 empty] | -91294.9741
-66680 | [7 empty] | -83954.6114
-55750 | [7 empty] | -70193.0052
-45800 | [7 empty] | -57665.285
-38960 | [7 empty] | -49053.2642
-33990 | [7 empty] | -42795.6995
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-90600 | [7 empty] | -114071.5026
-55510 | [7 empty] | -69890.829
-56970 | [7 empty] | -71729.0674
-63020 | [7 empty] | -79346.4249
-66990 | [7 empty] | -84344.9223
-67070 | [7 empty] | -84445.6477
-63170 | [7 empty] | -79535.285
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-75700 | [7 empty] | -95311.399
-50960 | [7 empty] | -64162.0725
-60750 | [7 empty] | -76488.342
-71800 | [7 empty] | -90401.0363
-78750 | [7 empty] | -99151.5544
-84440 | [7 empty] | -106315.6477
-88770 | [7 empty] | -111767.4093
-88910 | [7 empty] | -111943.6788
-88920 | [7 empty] | -111956.2694
-83830 | [7 empty] | -105547.6166
-74440 | [7 empty] | -93724.9741
-63680 | [7 empty] | -80177.4093
-52440 | [7 empty] | -66025.4922
-42870 | [7 empty] | -53976.2176
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-56770 | [7 empty] | -71477.2539
-36750 | [7 empty] | -46270.7254
-48790 | [7 empty] | -61429.8964
-60610 | [7 empty] | -76312.0725
-65200 | [7 empty] | -82091.1917
-71320 | [7 empty] | -89796.6839
-75490 | [7 empty] | -95046.9948
-79770 | [7 empty] | -100435.8031
-79800 | [7 empty] | -100473.5751
-77540 | [7 empty] | -97628.0829
-71040 | [7 empty] | -89444.1451
-64960 | [7 empty] | -81789.0155
-54020 | [7 empty] | -68014.8187
-44350 | [7 empty] | -55839.6373
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-54010 | [7 empty] | -68002.228
-35710 | [7 empty] | -44961.2953
-47560 | [7 empty] | -59881.2435
-58760 | [7 empty] | -73982.7979
-66100 | [7 empty] | -83224.3523
-70380 | [7 empty] | -88613.1606
-78680 | [7 empty] | -99063.4197
-83910 | [7 empty] | -105648.342
-85370 | [7 empty] | -107486.5803
-85940 | [7 empty] | -108204.2487
-80960 | [7 empty] | -101934.0933
-71350 | [7 empty] | -89834.456
-58650 | [7 empty] | -73844.3005
-47220 | [7 empty] | -59453.1606
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-44360 | [7 empty] | -55852.228
-25490 | [7 empty] | -32093.6269
-32770 | [7 empty] | -41259.6373
-44610 | [7 empty] | -56166.9948
-53200 | [7 empty] | -66982.3834
-64400 | [7 empty] | -81083.9378
-71740 | [7 empty] | -90325.4922
-77000 | [7 empty] | -96948.1865
-78160 | [7 empty] | -98408.7047
-75930 | [7 empty] | -95600.9845
-70990 | [7 empty] | -89381.1917
-62070 | [7 empty] | -78150.3109
-51310 | [7 empty] | -64602.7461
-40660 | [7 empty] | -51193.6788
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-39810 | [7 empty] | -50123.4715
-24310 | [7 empty] | -30607.9275
-37250 | [7 empty] | -46900.2591
-50730 | [7 empty] | -63872.487
-60960 | [7 empty] | -76752.7461
-68150 | [7 empty] | -85805.4404
-64100 | [7 empty] | -80706.2176
-74840 | [7 empty] | -94228.601
-74940 | [7 empty] | -94354.5078
-77080 | [7 empty] | -97048.9119
-73390 | [7 empty] | -92402.9534
-64670 | [7 empty] | -81423.886
-52400 | [7 empty] | -65975.1295
-40230 | [7 empty] | -50652.2798
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-53710 | [7 empty] | -67624.5078
-33780 | [7 empty] | -42531.2953
-35670 | [7 empty] | -44910.9326
-41870 | [7 empty] | -52717.1503
-49070 | [7 empty] | -61782.4352
-52730 | [7 empty] | -66390.6218
-58630 | [7 empty] | -73819.1192
-56790 | [7 empty] | -71502.4352
-57750 | [7 empty] | -72711.1399
-54710 | [7 empty] | -68883.5751
-46230 | [7 empty] | -58206.6839
-38930 | [7 empty] | -49015.4922
-32170 | [7 empty] | -40504.1969
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-79590 | [7 empty] | -100209.171
-58960 | [7 empty] | -74234.6114
-60280 | [7 empty] | -75896.5803
-59090 | [7 empty] | -74398.2902
-58910 | [7 empty] | -74171.658
-55120 | [7 empty] | -69399.7927
-50620 | [7 empty] | -63733.9896
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-59250 | [7 empty] | -74599.7409
-38300 | [7 empty] | -48222.2798
-48360 | [7 empty] | -60888.4974
-58840 | [7 empty] | -74083.5233
-67900 | [7 empty] | -85490.6736
-74100 | [7 empty] | -93296.8912
-78790 | [7 empty] | -99201.9171
-82080 | [7 empty] | -103344.2487
-83180 | [7 empty] | -104729.2228
-79390 | [7 empty] | -99957.3575
-74360 | [7 empty] | -93624.2487
-64790 | [7 empty] | -81574.9741
-53160 | [7 empty] | -66932.0207
-43280 | [7 empty] | -54492.4352
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-57390 | [7 empty] | -72257.8756
-36280 | [7 empty] | -45678.9637
-42520 | [7 empty] | -53535.544
-50010 | [7 empty] | -62965.9585
-58260 | [7 empty] | -73353.2642
-67090 | [7 empty] | -84470.829
-65520 | [7 empty] | -82494.0933
-74100 | [7 empty] | -93296.8912
-69940 | [7 empty] | -88059.171
-71420 | [7 empty] | -89922.5907
-65780 | [7 empty] | -82821.4508
-57620 | [7 empty] | -72547.4611
-48170 | [7 empty] | -60649.2746
-39360 | [7 empty] | -49556.8912
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-58750 | [7 empty] | -73970.2073
-39330 | [7 empty] | -49519.1192
-46870 | [7 empty] | -59012.487
-56730 | [7 empty] | -71426.8912
-62040 | [7 empty] | -78112.5389
-68640 | [7 empty] | -86422.3834
-75580 | [7 empty] | -95160.3109
-79860 | [7 empty] | -100549.1192
-79560 | [7 empty] | -100171.399
-78480 | [7 empty] | -98811.6062
-74390 | [7 empty] | -93662.0207
-65190 | [7 empty] | -82078.601
-53920 | [7 empty] | -67888.9119
-43950 | [7 empty] | -55336.0104
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-58830 | [7 empty] | -74070.9326
-37730 | [7 empty] | -47504.6114
-45340 | [7 empty] | -57086.114
-52470 | [7 empty] | -66063.2642
-64920 | [7 empty] | -81738.6528
-70350 | [7 empty] | -88575.3886
-76880 | [7 empty] | -96797.0984
-80740 | [7 empty] | -101657.0984
-80940 | [7 empty] | -101908.9119
-78790 | [7 empty] | -99201.9171
-75020 | [7 empty] | -94455.2332
-66130 | [7 empty] | -83262.1244
-54910 | [7 empty] | -69135.3886
-43790 | [7 empty] | -55134.5596
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-53840 | [7 empty] | -67788.1865
-35480 | [7 empty] | -44671.7098
-46420 | [7 empty] | -58445.9067
-59040 | [7 empty] | -74335.3368
-66560 | [7 empty] | -83803.5233
-73770 | [7 empty] | -92881.399
-78530 | [7 empty] | -98874.5596
-81510 | [7 empty] | -102626.5803
-82210 | [7 empty] | -103507.9275
-80190 | [7 empty] | -100964.6114
-74260 | [7 empty] | -93498.342
-65070 | [7 empty] | -81927.513
-54290 | [7 empty] | -68354.7668
-44490 | [7 empty] | -56015.9067
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-57670 | [7 empty] | -72610.4145
-35150 | [7 empty] | -44256.2176
-36310 | [7 empty] | -45716.7358
-45750 | [7 empty] | -57602.3316
-51660 | [7 empty] | -65043.4197
-56150 | [7 empty] | -70696.6321
-61600 | [7 empty] | -77558.5492
-63150 | [7 empty] | -79510.1036
-59680 | [7 empty] | -75141.1399
-56360 | [7 empty] | -70961.0363
-49510 | [7 empty] | -62336.4249
-41670 | [7 empty] | -52465.3368
-35010 | [7 empty] | -44079.9482
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-82000 | [7 empty] | -103243.5233
-63730 | [7 empty] | -80240.3627
-65740 | [7 empty] | -82771.0881
-59460 | [7 empty] | -74864.1451
-61510 | [7 empty] | -77445.2332
-60620 | [7 empty] | -76324.6632
-55420 | [7 empty] | -69777.513
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-62480 | [7 empty] | -78666.5285
-39660 | [7 empty] | -49934.6114
-50660 | [7 empty] | -63784.3523
-63450 | [7 empty] | -79887.8238
-69740 | [7 empty] | -87807.3575
-75190 | [7 empty] | -94669.2746
-77980 | [7 empty] | -98182.0725
-84990 | [7 empty] | -107008.1347
-87590 | [7 empty] | -110281.7098
-82400 | [7 empty] | -103747.1503
-77610 | [7 empty] | -97716.2176
-67670 | [7 empty] | -85201.0881
-57050 | [7 empty] | -71829.7927
-46730 | [7 empty] | -58836.2176
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-63650 | [7 empty] | -80139.6373
-40800 | [7 empty] | -51369.9482
-50060 | [7 empty] | -63028.9119
-62820 | [7 empty] | -79094.6114
-72000 | [7 empty] | -90652.8497
-79810 | [7 empty] | -100486.1658
-85580 | [7 empty] | -107750.9845
-88780 | [7 empty] | -111780
-78230 | [7 empty] | -98496.8394
-72830 | [7 empty] | -91697.8756
-69730 | [7 empty] | -87794.7668
-60260 | [7 empty] | -75871.399
-50400 | [7 empty] | -63456.9948
-41100 | [7 empty] | -51747.6684
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-52590 | [7 empty] | -66214.3523
-32490 | [7 empty] | -40907.0984
-42560 | [7 empty] | -53585.9067
-53830 | [7 empty] | -67775.5959
-63350 | [7 empty] | -79761.9171
-71220 | [7 empty] | -89670.7772
-75930 | [7 empty] | -95600.9845
-78930 | [7 empty] | -99378.1865
-79640 | [7 empty] | -100272.1244
-76760 | [7 empty] | -96646.0104
-69850 | [7 empty] | -87945.8549
-59960 | [7 empty] | -75493.6788
-48460 | [7 empty] | -61014.4041
-37800 | [7 empty] | -47592.7461
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-32690 | [7 empty] | -41158.9119
-19050 | [7 empty] | -23985.2332
-31380 | [7 empty] | -39509.5337
-43580 | [7 empty] | -54870.1554
-52160 | [7 empty] | -65672.9534
-59100 | [7 empty] | -74410.8808
-58280 | [7 empty] | -73378.4456
-58760 | [7 empty] | -73982.7979
-63470 | [7 empty] | -79913.0052
-61230 | [7 empty] | -77092.6943
-57600 | [7 empty] | -72522.2798
-49020 | [7 empty] | -61719.4819
-38000 | [7 empty] | -47844.5596
-26380 | [7 empty] | -33214.1969
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-18780 | [7 empty] | -23645.285
-13130 | [7 empty] | -16531.5544
-28340 | [7 empty] | -35681.9689
-43360 | [7 empty] | -54593.1606
-54770 | [7 empty] | -68959.1192
-63570 | [7 empty] | -80038.9119
-70070 | [7 empty] | -88222.8497
-75800 | [7 empty] | -95437.3057
-78270 | [7 empty] | -98547.2021
-77500 | [7 empty] | -97577.7202
-71930 | [7 empty] | -90564.715
-61690 | [7 empty] | -77671.8653
-49120 | [7 empty] | -61845.3886
-37250 | [7 empty] | -46900.2591
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-44430 | [7 empty] | -55940.3627
-34850 | [7 empty] | -43878.4974
-43560 | [7 empty] | -54844.9741
-49460 | [7 empty] | -62273.4715
-51010 | [7 empty] | -64225.0259
-52390 | [7 empty] | -65962.5389
-52410 | [7 empty] | -65987.7202
-50740 | [7 empty] | -63885.0777
-54940 | [7 empty] | -69173.1606
-52880 | [7 empty] | -66579.4819
-46570 | [7 empty] | -58634.7668
-37280 | [7 empty] | -46938.0311
-29500 | [7 empty] | -37142.487
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-55090 | [7 empty] | -69362.0207
-37720 | [7 empty] | -47492.0207
-36980 | [7 empty] | -46560.3109
-36970 | [7 empty] | -46547.7202
-36690 | [7 empty] | -46195.1813
-36100 | [7 empty] | -45452.3316
-33820 | [7 empty] | -42581.658
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-37000 | [7 empty] | -46585.4922
-21380 | [7 empty] | -26918.8601
-27690 | [7 empty] | -34863.5751
-33300 | [7 empty] | -41926.943
-35920 | [7 empty] | -45225.6995
-38170 | [7 empty] | -48058.601
-40110 | [7 empty] | -50501.1917
-42630 | [7 empty] | -53674.0415
-43020 | [7 empty] | -54165.0777
-48610 | [7 empty] | -61203.2642
-45690 | [7 empty] | -57526.7876
-39680 | [7 empty] | -49959.7927
-31620 | [7 empty] | -39811.7098
-24330 | [7 empty] | -30633.1088
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-37980 | [7 empty] | -47819.3782
-24230 | [7 empty] | -30507.2021
-32160 | [7 empty] | -40491.6062
-38840 | [7 empty] | -48902.1762
-44180 | [7 empty] | -55625.5959
-47260 | [7 empty] | -59503.5233
-51110 | [7 empty] | -64350.9326
-52940 | [7 empty] | -66655.0259
-54400 | [7 empty] | -68493.2642
-53410 | [7 empty] | -67246.7876
-51900 | [7 empty] | -65345.5959
-45530 | [7 empty] | -57325.3368
-35030 | [7 empty] | -44105.1295
-26520 | [7 empty] | -33390.4663
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-33000 | [7 empty] | -41549.2228
-20950 | [7 empty] | -26377.4611
-34180 | [7 empty] | -43034.9223
-46650 | [7 empty] | -58735.4922
-55460 | [7 empty] | -69827.8756
-61200 | [7 empty] | -77054.9223
-67820 | [7 empty] | -85389.9482
-70660 | [7 empty] | -88965.6995
-70810 | [7 empty] | -89154.5596
-71600 | [7 empty] | -90149.2228
-66260 | [7 empty] | -83425.8031
-56750 | [7 empty] | -71452.0725
-44940 | [7 empty] | -56582.487
-33970 | [7 empty] | -42770.5181
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-37680 | [7 empty] | -47441.658
-25470 | [7 empty] | -32068.4456
-37650 | [7 empty] | -47403.886
-51410 | [7 empty] | -64728.6528
-62730 | [7 empty] | -78981.2953
-67860 | [7 empty] | -85440.3109
-71800 | [7 empty] | -90401.0363
-75070 | [7 empty] | -94518.1865
-79700 | [7 empty] | -100347.6684
-74130 | [7 empty] | -93334.6632
-66220 | [7 empty] | -83375.4404
-57260 | [7 empty] | -72094.1969
-47270 | [7 empty] | -59516.114
-38450 | [7 empty] | -48411.1399
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-50210 | [7 empty] | -63217.772
-31070 | [7 empty] | -39119.2228
-37760 | [7 empty] | -47542.3834
-43360 | [7 empty] | -54593.1606
-52090 | [7 empty] | -65584.8187
-62230 | [7 empty] | -78351.7617
-69330 | [7 empty] | -87291.1399
-74240 | [7 empty] | -93473.1606
-76150 | [7 empty] | -95877.9793
-74790 | [7 empty] | -94165.6477
-68800 | [7 empty] | -86623.8342
-58380 | [7 empty] | -73504.3523
-46200 | [7 empty] | -58168.9119
-36390 | [7 empty] | -45817.4611
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-48520 | [7 empty] | -61089.9482
-29470 | [7 empty] | -37104.715
-32250 | [7 empty] | -40604.9223
-35580 | [7 empty] | -44797.6166
-38100 | [7 empty] | -47970.4663
-39050 | [7 empty] | -49166.5803
-39320 | [7 empty] | -49506.5285
-45030 | [7 empty] | -56695.8031
-45920 | [7 empty] | -57816.3731
-40210 | [7 empty] | -50627.0984
-32780 | [7 empty] | -41272.228
-26960 | [7 empty] | -33944.456
-23340 | [7 empty] | -29386.6321
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-39630 | [7 empty] | -49896.8394
-27040 | [7 empty] | -34045.1813
-28270 | [7 empty] | -35593.8342
-28570 | [7 empty] | -35971.5544
-28510 | [7 empty] | -35896.0104
-27960 | [7 empty] | -35203.5233
-26760 | [7 empty] | -33692.6425
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-29270 | [7 empty] | -36852.9016
-19290 | [7 empty] | -24287.4093
-33430 | [7 empty] | -42090.6218
-44380 | [7 empty] | -55877.4093
-52430 | [7 empty] | -66012.9016
-59630 | [7 empty] | -75078.1865
-61840 | [7 empty] | -77860.7254
-70600 | [7 empty] | -88890.1554
-71590 | [7 empty] | -90136.6321
-71330 | [7 empty] | -89809.2746
-66590 | [7 empty] | -83841.2953
-57590 | [7 empty] | -72509.6891
-46160 | [7 empty] | -58118.5492
-36510 | [7 empty] | -45968.5492
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-43470 | [7 empty] | -54731.658
-27560 | [7 empty] | -34699.8964
-34720 | [7 empty] | -43714.8187
-39820 | [7 empty] | -50136.0622
-43810 | [7 empty] | -55159.7409
-46200 | [7 empty] | -58168.9119
-48070 | [7 empty] | -60523.3679
-51330 | [7 empty] | -64627.9275
-51490 | [7 empty] | -64829.3782
-49820 | [7 empty] | -62726.7358
-45280 | [7 empty] | -57010.5699
-38190 | [7 empty] | -48083.7824
-30240 | [7 empty] | -38074.1969
-23440 | [7 empty] | -29512.5389
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-26750 | [7 empty] | -33680.0518
-15320 | [7 empty] | -19288.9119
-23820 | [7 empty] | -29990.9845
-33870 | [7 empty] | -42644.6114
-37240 | [7 empty] | -46887.6684
-42490 | [7 empty] | -53497.772
-45460 | [7 empty] | -57237.2021
-47540 | [7 empty] | -59856.0622
-48290 | [7 empty] | -60800.3627
-48450 | [7 empty] | -61001.8135
-43710 | [7 empty] | -55033.8342
-37510 | [7 empty] | -47227.6166
-30710 | [7 empty] | -38665.9585
-23290 | [7 empty] | -29323.6788
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-28530 | [7 empty] | -35921.1917
-18620 | [7 empty] | -23443.8342
-28100 | [7 empty] | -35379.7927
-38820 | [7 empty] | -48876.9948
-47440 | [7 empty] | -59730.1554
-55890 | [7 empty] | -70369.2746
-60590 | [7 empty] | -76286.8912
-62420 | [7 empty] | -78590.9845
-64570 | [7 empty] | -81297.9793
-63000 | [7 empty] | -79321.2435
-61610 | [7 empty] | -77571.1399
-53630 | [7 empty] | -67523.7824
-43460 | [7 empty] | -54719.0674
-34180 | [7 empty] | -43034.9223
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-40900 | [7 empty] | -51495.8549
-27550 | [7 empty] | -34687.3057
-34440 | [7 empty] | -43362.2798
-43180 | [7 empty] | -54366.5285
-55150 | [7 empty] | -69437.5648
-61500 | [7 empty] | -77432.6425
-67230 | [7 empty] | -84647.0984
-72970 | [7 empty] | -91874.1451
-73980 | [7 empty] | -93145.8031
-72480 | [7 empty] | -91257.2021
-66520 | [7 empty] | -83753.1606
-56150 | [7 empty] | -70696.6321
-44760 | [7 empty] | -56355.8549
-36100 | [7 empty] | -45452.3316
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-47320 | [7 empty] | -59579.0674
-32790 | [7 empty] | -41284.8187
-39760 | [7 empty] | -50060.5181
-46350 | [7 empty] | -58357.772
-53040 | [7 empty] | -66780.9326
-56210 | [7 empty] | -70772.1762
-59680 | [7 empty] | -75141.1399
-59200 | [7 empty] | -74536.7876
-56300 | [7 empty] | -70885.4922
-50860 | [7 empty] | -64036.1658
-44950 | [7 empty] | -56595.0777
-36640 | [7 empty] | -46132.228
-30850 | [7 empty] | -38842.228
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-75490 | [7 empty] | -95046.9948
-60960 | [7 empty] | -76752.7461
-63980 | [7 empty] | -80555.1295
-63470 | [7 empty] | -79913.0052
-57240 | [7 empty] | -72069.0155
-56270 | [7 empty] | -70847.7202
-52970 | [7 empty] | -66692.7979
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-46670 | [7 empty] | -58760.6736
-26840 | [7 empty] | -33793.3679
-39000 | [7 empty] | -49103.6269
-50600 | [7 empty] | -63708.8083
-59790 | [7 empty] | -75279.6373
-67540 | [7 empty] | -85037.4093
-71810 | [7 empty] | -90413.6269
-76390 | [7 empty] | -96180.1554
-77310 | [7 empty] | -97338.4974
-74960 | [7 empty] | -94379.6891
-68460 | [7 empty] | -86195.7513
-57180 | [7 empty] | -71993.4715
-44880 | [7 empty] | -56506.943
-34930 | [7 empty] | -43979.2228
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-40620 | [7 empty] | -51143.3161
-25720 | [7 empty] | -32383.2124
-37270 | [7 empty] | -46925.4404
-46200 | [7 empty] | -58168.9119
-54690 | [7 empty] | -68858.3938
-57630 | [7 empty] | -72560.0518
-64100 | [7 empty] | -80706.2176
-69170 | [7 empty] | -87089.6891
-69940 | [7 empty] | -88059.171
-67660 | [7 empty] | -85188.4974
-60110 | [7 empty] | -75682.5389
-48570 | [7 empty] | -61152.9016
-36140 | [7 empty] | -45502.6943
-25480 | [7 empty] | -32081.0363
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-14660 | [7 empty] | -18457.9275
-6230 | [7 empty] | -7843.9896
-17400 | [7 empty] | -21907.772
-33200 | [7 empty] | -41801.0363
-44480 | [7 empty] | -56003.3161
-53070 | [7 empty] | -66818.7047
-58670 | [7 empty] | -73869.4819
-62770 | [7 empty] | -79031.658
-63460 | [7 empty] | -79900.4145
-62810 | [7 empty] | -79082.0207
-57230 | [7 empty] | -72056.4249
-47040 | [7 empty] | -59226.5285
-35880 | [7 empty] | -45175.3368
-26890 | [7 empty] | -33856.3212
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-17430 | [7 empty] | -21945.544
-7280 | [7 empty] | -9166.0104
-13880 | [7 empty] | -17475.8549
-23190 | [7 empty] | -29197.772
-29690 | [7 empty] | -37381.7098
-32340 | [7 empty] | -40718.2383
-31760 | [7 empty] | -39987.9793
-32860 | [7 empty] | -41372.9534
-33160 | [7 empty] | -41750.6736
-31110 | [7 empty] | -39169.5855
-26090 | [7 empty] | -32849.0674
-20300 | [7 empty] | -25559.0674
-13300 | [7 empty] | -16745.5959
-6890 | [7 empty] | -8674.9741
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-4290 | [7 empty] | -5401.399
600 | [7 empty] | 451.1166
-1840 | [7 empty] | -2316.6839
-6710 | [7 empty] | -8448.342
-20510 | [7 empty] | -25823.4715
-31720 | [7 empty] | -39937.6166
-38140 | [7 empty] | -48020.829
-42640 | [7 empty] | -53686.6321
-43780 | [7 empty] | -55121.9689
-42110 | [7 empty] | -53019.3264
-36200 | [7 empty] | -45578.2383
-27160 | [7 empty] | -34196.2694
-16740 | [7 empty] | -21076.7876
-6790 | [7 empty] | -8549.0674
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-2280 | [7 empty] | -2870.6736
-90 | [7 empty] | -113.3161
-840 | [7 empty] | -1057.6166
-6320 | [7 empty] | -7957.3057
-18370 | [7 empty] | -23129.0674
-26970 | [7 empty] | -33957.0466
-31290 | [7 empty] | -39396.2176
-29620 | [7 empty] | -37293.5751
-25700 | [7 empty] | -32358.0311
-22620 | [7 empty] | -28480.1036
-18620 | [7 empty] | -23443.8342
-13360 | [7 empty] | -16821.1399
-8900 | [7 empty] | -11205.6995
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-16990 | [7 empty] | -21391.5544
-18840 | [7 empty] | -23720.829
-24720 | [7 empty] | -31124.1451
-28990 | [7 empty] | -36500.3627
-30630 | [7 empty] | -38565.2332
-29210 | [7 empty] | -36777.3575
-25050 | [7 empty] | -31539.6373
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-5910 | [7 empty] | -7441.0881
-1160 | [7 empty] | -1460.5181
-6600 | [7 empty] | -8309.8446
-23460 | [7 empty] | -29537.7202
-35090 | [7 empty] | -44180.6736
-47370 | [7 empty] | -59642.0207
-55690 | [7 empty] | -70117.4611
-61550 | [7 empty] | -77495.5959
-63950 | [7 empty] | -80517.3575
-62720 | [7 empty] | -78968.7047
-56720 | [7 empty] | -71414.3005
-46090 | [7 empty] | -58030.4145
-35550 | [7 empty] | -44759.8446
-27090 | [7 empty] | -34108.1347
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-15580 | [7 empty] | -19616.2694
-8070 | [7 empty] | -10160.6736
-21620 | [7 empty] | -27221.0363
-35180 | [7 empty] | -44293.9896
-46160 | [7 empty] | -58118.5492
-51070 | [7 empty] | -64300.5699
-53910 | [7 empty] | -67876.3212
-59220 | [7 empty] | -74561.9689
-61000 | [7 empty] | -76803.1088
-60540 | [7 empty] | -76223.9378
-54490 | [7 empty] | -68606.5803
-44930 | [7 empty] | -56569.8964
-35860 | [7 empty] | -45150.1554
-27940 | [7 empty] | -35178.342
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-13440 | [7 empty] | -16921.8653
-2450 | [7 empty] | -3084.715
-4680 | [7 empty] | -5892.4352
-10230 | [7 empty] | -12880.2591
-18370 | [7 empty] | -23129.0674
-27530 | [7 empty] | -34662.1244
-33790 | [7 empty] | -42543.886
-39110 | [7 empty] | -49242.1244
-39960 | [7 empty] | -50312.3316
-38170 | [7 empty] | -48058.601
-31870 | [7 empty] | -40126.4767
-22050 | [7 empty] | -27762.4352
-10080 | [7 empty] | -12691.399
-2670 | [7 empty] | -3361.7098
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-1490 | [7 empty] | -1876.0104
2400 | [7 empty] | 1804.4665
-1550 | [7 empty] | -1951.5544
-4910 | [7 empty] | -6182.0207
-16660 | [7 empty] | -20976.0622
-28360 | [7 empty] | -35707.1503
-35490 | [7 empty] | -44684.3005
-41970 | [7 empty] | -52843.057
-44330 | [7 empty] | -55814.456
-42510 | [7 empty] | -53522.9534
-37930 | [7 empty] | -47756.4249
-29120 | [7 empty] | -36664.0415
-19570 | [7 empty] | -24639.9482
-10970 | [7 empty] | -13811.9689
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-5770 | [7 empty] | -7264.8187
-930 | [7 empty] | -1170.9326
-3150 | [7 empty] | -3966.0622
-17120 | [7 empty] | -21555.2332
-32110 | [7 empty] | -40428.6528
-43910 | [7 empty] | -55285.6477
-52030 | [7 empty] | -65509.2746
-57720 | [7 empty] | -72673.3679
-59560 | [7 empty] | -74990.0518
-62560 | [7 empty] | -78767.2539
-57470 | [7 empty] | -72358.601
-43880 | [7 empty] | -55247.8756
-33140 | [7 empty] | -41725.4922
-24190 | [7 empty] | -30456.8394
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-16660 | [7 empty] | -20976.0622
-10780 | [7 empty] | -13572.7461
-17090 | [7 empty] | -21517.4611
-25830 | [7 empty] | -32521.7098
-31930 | [7 empty] | -40202.0207
-36240 | [7 empty] | -45628.601
-37420 | [7 empty] | -47114.3005
-32140 | [7 empty] | -40466.4249
-27790 | [7 empty] | -34989.4819
-23150 | [7 empty] | -29147.4093
-14470 | [7 empty] | -18218.7047
-6590 | [7 empty] | -8297.2539
-1820 | [7 empty] | -2291.5026
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-2280 | [7 empty] | -2870.6736
-140 | [7 empty] | -176.2694
-3690 | [7 empty] | -4645.9585
-7250 | [7 empty] | -9128.2383
-10810 | [7 empty] | -13610.5181
-10590 | [7 empty] | -13333.5233
-7350 | [7 empty] | -9254.1451
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
7630 | [7 empty] | 5736.6998
7310 | [7 empty] | 5496.1042
140 | [7 empty] | 105.2605
-910 | [7 empty] | -1145.7513
-5370 | [7 empty] | -6761.1917
-17860 | [7 empty] | -22486.943
-27450 | [7 empty] | -34561.399
-34190 | [7 empty] | -43047.513
-37180 | [7 empty] | -46812.1244
-37120 | [7 empty] | -46736.5803
-32260 | [7 empty] | -40617.513
-22940 | [7 empty] | -28883.0052
-14230 | [7 empty] | -17916.5285
-7070 | [7 empty] | -8901.6062
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-3440 | [7 empty] | -4331.1917
40 | [7 empty] | 30.0744
-1200 | [7 empty] | -1510.8808
-4620 | [7 empty] | -5816.8912
-19720 | [7 empty] | -24828.8083
-30270 | [7 empty] | -38111.9689
-37240 | [7 empty] | -46887.6684
-42090 | [7 empty] | -52994.1451
-44450 | [7 empty] | -55965.544
-44120 | [7 empty] | -55550.0518
-39900 | [7 empty] | -50236.7876
-31750 | [7 empty] | -39975.3886
-23480 | [7 empty] | -29562.9016
-16190 | [7 empty] | -20384.3005
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-9260 | [7 empty] | -11658.9637
-3800 | [7 empty] | -4784.456
-15260 | [7 empty] | -19213.3679
-28880 | [7 empty] | -36361.8653
-39160 | [7 empty] | -49305.0777
-44740 | [7 empty] | -56330.6736
-54230 | [7 empty] | -68279.2228
-56470 | [7 empty] | -71099.5337
-56920 | [7 empty] | -71666.114
-55360 | [7 empty] | -69701.9689
-49090 | [7 empty] | -61807.6166
-39460 | [7 empty] | -49682.7979
-30500 | [7 empty] | -38401.5544
-23290 | [7 empty] | -29323.6788
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-15030 | [7 empty] | -18923.7824
-7310 | [7 empty] | -9203.7824
-20220 | [7 empty] | -25458.342
-33060 | [7 empty] | -41624.7668
-42610 | [7 empty] | -53648.8601
-46710 | [7 empty] | -58811.0363
-48850 | [7 empty] | -61505.4404
-55450 | [7 empty] | -69815.285
-57700 | [7 empty] | -72648.1865
-57890 | [7 empty] | -72887.4093
-52550 | [7 empty] | -66163.9896
-42730 | [7 empty] | -53799.9482
-33630 | [7 empty] | -42342.4352
-26090 | [7 empty] | -32849.0674
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-23280 | [7 empty] | -29311.0881
-12750 | [7 empty] | -16053.1088
-21770 | [7 empty] | -27409.8964
-28100 | [7 empty] | -35379.7927
-31650 | [7 empty] | -39849.4819
-35150 | [7 empty] | -44256.2176
-44190 | [7 empty] | -55638.1865
-49970 | [7 empty] | -62915.5959
-52070 | [7 empty] | -65559.6373
-51210 | [7 empty] | -64476.8394
-49870 | [7 empty] | -62789.6891
-41740 | [7 empty] | -52553.4715
-33890 | [7 empty] | -42669.7927
-26960 | [7 empty] | -33944.456
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-30610 | [7 empty] | -38540.0518
-17570 | [7 empty] | -22121.8135
-19230 | [7 empty] | -24211.8653
-23840 | [7 empty] | -30016.1658
-27790 | [7 empty] | -34989.4819
-29490 | [7 empty] | -37129.8964
-31650 | [7 empty] | -39849.4819
-34780 | [7 empty] | -43790.3627
-36950 | [7 empty] | -46522.5389
-33950 | [7 empty] | -42745.3368
-28210 | [7 empty] | -35518.2902
-22810 | [7 empty] | -28719.3264
-18450 | [7 empty] | -23229.7927
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-40170 | [7 empty] | -50576.7358
-31090 | [7 empty] | -39144.4041
-36060 | [7 empty] | -45401.9689
-39740 | [7 empty] | -50035.3368
-40280 | [7 empty] | -50715.2332
-40090 | [7 empty] | -50476.0104
-36270 | [7 empty] | -45666.3731
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-32360 | [7 empty] | -40743.4197
-19070 | [7 empty] | -24010.4145
-25000 | [7 empty] | -31476.6839
-32180 | [7 empty] | -40516.7876
-40780 | [7 empty] | -51344.7668
-46360 | [7 empty] | -58370.3627
-53940 | [7 empty] | -67914.0933
-56060 | [7 empty] | -70583.3161
-60710 | [7 empty] | -76437.9793
-59930 | [7 empty] | -75455.9067
-53980 | [7 empty] | -67964.456
-45770 | [7 empty] | -57627.513
-37020 | [7 empty] | -46610.6736
-29570 | [7 empty] | -37230.6218
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-26100 | [7 empty] | -32861.658
-10350 | [7 empty] | -13031.3472
-15850 | [7 empty] | -19956.2176
-18620 | [7 empty] | -23443.8342
-22290 | [7 empty] | -28064.6114
-30830 | [7 empty] | -38817.0466
-38250 | [7 empty] | -48159.3264
-44380 | [7 empty] | -55877.4093
-46550 | [7 empty] | -58609.5855
-44840 | [7 empty] | -56456.5803
-38530 | [7 empty] | -48511.8653
-27740 | [7 empty] | -34926.5285
-16240 | [7 empty] | -20447.2539
-7440 | [7 empty] | -9367.4611
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
430 | [7 empty] | 323.3002
4560 | [7 empty] | 3428.4864
-990 | [7 empty] | -1246.4767
-2310 | [7 empty] | -2908.4456
-9420 | [7 empty] | -11860.4145
-21600 | [7 empty] | -27195.8549
-28960 | [7 empty] | -36462.5907
-35340 | [7 empty] | -44495.4404
-37890 | [7 empty] | -47706.0622
-36750 | [7 empty] | -46270.7254
-30930 | [7 empty] | -38942.9534
-20320 | [7 empty] | -25584.2487
-9720 | [7 empty] | -12238.1347
-2660 | [7 empty] | -3349.1192
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
3940 | [7 empty] | 2962.3325
7420 | [7 empty] | 5578.8089
1340 | [7 empty] | 1007.4938
-1280 | [7 empty] | -1611.6062
-4160 | [7 empty] | -5237.7202
-13710 | [7 empty] | -17261.8135
-24320 | [7 empty] | -30620.5181
-31700 | [7 empty] | -39912.4352
-34650 | [7 empty] | -43626.6839
-34340 | [7 empty] | -43236.3731
-29630 | [7 empty] | -37306.1658
-19870 | [7 empty] | -25017.6684
-9710 | [7 empty] | -12225.544
-2570 | [7 empty] | -3235.8031
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
2980 | [7 empty] | 2240.5459
4270 | [7 empty] | 3210.4467
-400 | [7 empty] | -503.6269
-1940 | [7 empty] | -2442.5907
-8050 | [7 empty] | -10135.4922
-21200 | [7 empty] | -26692.228
-27970 | [7 empty] | -35216.114
-34230 | [7 empty] | -43097.8756
-37310 | [7 empty] | -46975.8031
-36070 | [7 empty] | -45414.5596
-30690 | [7 empty] | -38640.7772
-20910 | [7 empty] | -26327.0984
-9950 | [7 empty] | -12527.7202
-2660 | [7 empty] | -3349.1192
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
1030 | [7 empty] | 774.4169
1410 | [7 empty] | 1060.1241
0 | [7 empty] | 0
-330 | [7 empty] | -415.4922
-4600 | [7 empty] | -5791.7098
-14200 | [7 empty] | -17878.7565
-21330 | [7 empty] | -26855.9067
-24460 | [7 empty] | -30796.7876
-23890 | [7 empty] | -30079.1192
-19770 | [7 empty] | -24891.7617
-12960 | [7 empty] | -16317.513
-7370 | [7 empty] | -9279.3264
-3370 | [7 empty] | -4243.057
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-3470 | [7 empty] | -4368.9637
-8870 | [7 empty] | -11167.9275
-16860 | [7 empty] | -21227.8756
-22560 | [7 empty] | -28404.5596
-24960 | [7 empty] | -31426.3212
-23970 | [7 empty] | -30179.8446
-20030 | [7 empty] | -25219.1192
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-6030 | [7 empty] | -7592.1762
-1590 | [7 empty] | -2001.9171
-3930 | [7 empty] | -4948.1347
-9740 | [7 empty] | -12263.3161
-14970 | [7 empty] | -18848.2383
-18080 | [7 empty] | -22763.9378
-21900 | [7 empty] | -27573.5751
-22030 | [7 empty] | -27737.2539
-22040 | [7 empty] | -27749.8446
-22620 | [7 empty] | -28480.1036
-20590 | [7 empty] | -25924.1969
-16390 | [7 empty] | -20636.114
-9930 | [7 empty] | -12502.5389
-4290 | [7 empty] | -5401.399
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-6240 | [7 empty] | -7856.5803
-1810 | [7 empty] | -2278.9119
-5430 | [7 empty] | -6836.7358
-14670 | [7 empty] | -18470.5181
-20620 | [7 empty] | -25961.9689
-24800 | [7 empty] | -31224.8705
-27690 | [7 empty] | -34863.5751
-30620 | [7 empty] | -38552.6425
-31850 | [7 empty] | -40101.2953
-32300 | [7 empty] | -40667.8756
-28940 | [7 empty] | -36437.4093
-22610 | [7 empty] | -28467.513
-16270 | [7 empty] | -20485.0259
-10860 | [7 empty] | -13673.4715
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-12940 | [7 empty] | -16292.3316
-6060 | [7 empty] | -7629.9482
-13420 | [7 empty] | -16896.6839
-19420 | [7 empty] | -24451.0881
-24760 | [7 empty] | -31174.5078
-27740 | [7 empty] | -34926.5285
-29610 | [7 empty] | -37280.9845
-33270 | [7 empty] | -41889.171
-34170 | [7 empty] | -43022.3316
-33400 | [7 empty] | -42052.8497
-29690 | [7 empty] | -37381.7098
-24020 | [7 empty] | -30242.7979
-17290 | [7 empty] | -21769.2746
-11210 | [7 empty] | -14114.1451
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-8220 | [7 empty] | -10349.5337
-2290 | [7 empty] | -2883.2642
-6370 | [7 empty] | -8020.2591
-18300 | [7 empty] | -23040.9326
-24550 | [7 empty] | -30910.1036
-28950 | [7 empty] | -36450
-31580 | [7 empty] | -39761.3472
-31440 | [7 empty] | -39585.0777
-27900 | [7 empty] | -35127.9793
-20280 | [7 empty] | -25533.886
-11160 | [7 empty] | -14051.1917
-3910 | [7 empty] | -4922.9534
-1820 | [7 empty] | -2291.5026
-350 | [7 empty] | -440.6736
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
21420 | [7 empty] | 16104.8635
20010 | [7 empty] | 15044.7395
9330 | [7 empty] | 7014.8635
1820 | [7 empty] | 1368.3871
-120 | [7 empty] | -151.0881
-1250 | [7 empty] | -1573.8342
-5280 | [7 empty] | -6647.8756
-10140 | [7 empty] | -12766.943
-13120 | [7 empty] | -16518.9637
-12690 | [7 empty] | -15977.5648
-7850 | [7 empty] | -9883.6788
-1820 | [7 empty] | -2291.5026
-250 | [7 empty] | -314.7668
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
340 | [7 empty] | 255.6328
2400 | [7 empty] | 1804.4665
4240 | [7 empty] | 3187.8908
5680 | [7 empty] | 4270.5707
41240 | [7 empty] | 31006.7494
29780 | [7 empty] | 22390.4218
16660 | [7 empty] | 12526.005
6350 | [7 empty] | 4774.3176
1460 | [7 empty] | 1097.7171
0 | [7 empty] | 0
0 | [7 empty] | 0
-50 | [7 empty] | -62.9534
-190 | [7 empty] | -239.2228
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
90 | [7 empty] | 67.6675
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
940 | [7 empty] | 706.7494
2770 | [7 empty] | 2082.6551
4150 | [7 empty] | 3120.2233
4460 | [7 empty] | 3353.3002
1750 | [7 empty] | 1315.7568
0 | [7 empty] | 0
20180 | [7 empty] | 15172.5558
4270 | [7 empty] | 3210.4467
1240 | [7 empty] | 932.3077
300 | [7 empty] | 225.5583
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
13300 | [7 empty] | 9999.7519
8140 | [7 empty] | 6120.1489
620 | [7 empty] | 466.1538
0 | [7 empty] | 0
0 | [7 empty] | 0
-620 | [7 empty] | -780.6218
-4420 | [7 empty] | -5565.0777
-12370 | [7 empty] | -15574.6632
-16140 | [7 empty] | -20321.3472
-15230 | [7 empty] | -19175.5959
-10860 | [7 empty] | -13673.4715
-5000 | [7 empty] | -6295.3368
-1720 | [7 empty] | -2165.5959
-370 | [7 empty] | -465.8549
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-680 | [7 empty] | -856.1658
0 | [7 empty] | 0
0 | [7 empty] | 0
-1120 | [7 empty] | -1410.1554
-2620 | [7 empty] | -3298.7565
-12910 | [7 empty] | -16254.5596
-22230 | [7 empty] | -27989.0674
-24630 | [7 empty] | -31010.829
-28550 | [7 empty] | -35946.3731
-28460 | [7 empty] | -35833.057
-24160 | [7 empty] | -30419.0674
-16030 | [7 empty] | -20182.8497
-8670 | [7 empty] | -10916.114
-3420 | [7 empty] | -4306.0104
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-1630 | [7 empty] | -2052.2798
1110 | [7 empty] | 834.5658
-250 | [7 empty] | -314.7668
-1700 | [7 empty] | -2140.4145
-8020 | [7 empty] | -10097.7202
-20670 | [7 empty] | -26024.9223
-27210 | [7 empty] | -34259.2228
-32480 | [7 empty] | -40894.5078
-34090 | [7 empty] | -42921.6062
-32020 | [7 empty] | -40315.3368
-26710 | [7 empty] | -33629.6891
-17650 | [7 empty] | -22222.5389
-9110 | [7 empty] | -11470.1036
-2670 | [7 empty] | -3361.7098
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
2470 | [7 empty] | 1857.0968
5290 | [7 empty] | 3977.3449
150 | [7 empty] | 112.7792
-1260 | [7 empty] | -1586.4249
-4070 | [7 empty] | -5124.4041
-15420 | [7 empty] | -19414.8187
-24130 | [7 empty] | -30381.2953
-30750 | [7 empty] | -38716.3212
-33320 | [7 empty] | -41952.1244
-32170 | [7 empty] | -40504.1969
-26990 | [7 empty] | -33982.228
-16920 | [7 empty] | -21303.4197
-6080 | [7 empty] | -7655.1295
-1630 | [7 empty] | -2052.2798
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
8680 | [7 empty] | 6526.1538
8070 | [7 empty] | 6067.5186
1880 | [7 empty] | 1413.4988
-470 | [7 empty] | -591.7617
-1420 | [7 empty] | -1787.8756
-2020 | [7 empty] | -2543.3161
-8300 | [7 empty] | -10450.2591
-14300 | [7 empty] | -18004.6632
-16100 | [7 empty] | -20270.9845
-15970 | [7 empty] | -20107.3057
-12220 | [7 empty] | -15385.8031
-5800 | [7 empty] | -7302.5907
-2310 | [7 empty] | -2908.4456
-670 | [7 empty] | -843.5751
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-2120 | [7 empty] | -2669.2228
0 | [7 empty] | 0
-100 | [7 empty] | -125.9067
-810 | [7 empty] | -1019.8446
-1140 | [7 empty] | -1435.3368
-2130 | [7 empty] | -2681.8135
-9140 | [7 empty] | -11507.8756
-14260 | [7 empty] | -17954.3005
-15110 | [7 empty] | -19024.5078
-12290 | [7 empty] | -15473.9378
-6090 | [7 empty] | -7667.7202
-1550 | [7 empty] | -1951.5544
-390 | [7 empty] | -491.0363
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-1030 | [7 empty] | -1296.8394
0 | [7 empty] | 0
0 | [7 empty] | 0
-2320 | [7 empty] | -2921.0363
-6490 | [7 empty] | -8171.3472
-5880 | [7 empty] | -7403.3161
-1400 | [7 empty] | -1762.6943
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
14710 | [7 empty] | 11059.8759
13460 | [7 empty] | 10120.0496
5240 | [7 empty] | 3939.7519
0 | [7 empty] | 0
-100 | [7 empty] | -125.9067
-1310 | [7 empty] | -1649.3782
-7600 | [7 empty] | -9568.9119
-14890 | [7 empty] | -18747.513
-17060 | [7 empty] | -21479.6891
-15950 | [7 empty] | -20082.1244
-11020 | [7 empty] | -13874.9223
-2800 | [7 empty] | -3525.3886
-220 | [7 empty] | -276.9948
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
310 | [7 empty] | 233.0769
30240 | [7 empty] | 22736.2779
25970 | [7 empty] | 19525.8313
13890 | [7 empty] | 10443.3499
3210 | [7 empty] | 2413.4739
0 | [7 empty] | 0
0 | [7 empty] | 0
-90 | [7 empty] | -113.3161
-610 | [7 empty] | -768.0311
-430 | [7 empty] | -541.399
-200 | [7 empty] | -251.8135
0 | [7 empty] | 0
50 | [7 empty] | 37.5931
6250 | [7 empty] | 4699.1315
12670 | [7 empty] | 9526.0794
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
150 | [7 empty] | 112.7792
1560 | [7 empty] | 1172.9032
3140 | [7 empty] | 2360.8437
4570 | [7 empty] | 3436.005
5540 | [7 empty] | 4165.3102
6290 | [7 empty] | 4729.206
6960 | [7 empty] | 5232.9529
47280 | [7 empty] | 35547.9901
36860 | [7 empty] | 27713.598
25760 | [7 empty] | 19367.9404
14360 | [7 empty] | 10796.7246
4250 | [7 empty] | 3195.4094
540 | [7 empty] | 406.005
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
490 | [7 empty] | 368.4119
9630 | [7 empty] | 7240.4218
16320 | [7 empty] | 12270.3722
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
970 | [7 empty] | 729.3052
3940 | [7 empty] | 2962.3325
6840 | [7 empty] | 5142.7295
8880 | [7 empty] | 6676.5261
11350 | [7 empty] | 8533.6228
12950 | [7 empty] | 9736.6005
13720 | [7 empty] | 10315.5335
56280 | [7 empty] | 42314.7395
49330 | [7 empty] | 37089.3052
34810 | [7 empty] | 26172.2829
19650 | [7 empty] | 14774.0695
8180 | [7 empty] | 6150.2233
720 | [7 empty] | 541.34
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-760 | [7 empty] | -956.8912
-270 | [7 empty] | -339.9482
0 | [7 empty] | 0
0 | [7 empty] | 0
3900 | [7 empty] | 2932.2581
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
620 | [7 empty] | 466.1538
2590 | [7 empty] | 1947.3201
4650 | [7 empty] | 3496.1538
6590 | [7 empty] | 4954.7643
47340 | [7 empty] | 35593.1017
39990 | [7 empty] | 30066.9231
25520 | [7 empty] | 19187.4938
9080 | [7 empty] | 6826.8983
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-5580 | [7 empty] | -7025.5959
-11320 | [7 empty] | -14252.6425
-13010 | [7 empty] | -16380.4663
-8940 | [7 empty] | -11256.0622
-2350 | [7 empty] | -2958.8083
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
28260 | [7 empty] | 21247.5931
21440 | [7 empty] | 16119.9007
8550 | [7 empty] | 6428.4119
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-1520 | [7 empty] | -1913.7824
-4180 | [7 empty] | -5262.9016
-4050 | [7 empty] | -5099.2228
-1740 | [7 empty] | -2190.7772
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
1890 | [7 empty] | 1421.0174
0 | [7 empty] | 0
0 | [7 empty] | 0
-30 | [7 empty] | -37.772
-1940 | [7 empty] | -2442.5907
-2290 | [7 empty] | -2883.2642
-590 | [7 empty] | -742.8497
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
11660 | [7 empty] | 8766.6998
8470 | [7 empty] | 6368.263
110 | [7 empty] | 82.7047
0 | [7 empty] | 0
-2780 | [7 empty] | -3500.2073
-18520 | [7 empty] | -23317.9275
-27950 | [7 empty] | -35190.9326
-34590 | [7 empty] | -43551.1399
-37660 | [7 empty] | -47416.4767
-37780 | [7 empty] | -47567.5648
-32840 | [7 empty] | -41347.772
-22610 | [7 empty] | -28467.513
-12630 | [7 empty] | -15902.0207
-5640 | [7 empty] | -7101.1399
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-1440 | [7 empty] | -1813.057
1620 | [7 empty] | 1218.0149
0 | [7 empty] | 0
-1510 | [7 empty] | -1901.1917
-6350 | [7 empty] | -7995.0777
-19090 | [7 empty] | -24035.5959
-24630 | [7 empty] | -31010.829
-28930 | [7 empty] | -36424.8187
-31610 | [7 empty] | -39799.1192
-29390 | [7 empty] | -37003.9896
-26230 | [7 empty] | -33025.3368
-19080 | [7 empty] | -24023.0052
-12300 | [7 empty] | -15486.5285
-6040 | [7 empty] | -7604.7668
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-4660 | [7 empty] | -5867.2539
-510 | [7 empty] | -642.1244
-1690 | [7 empty] | -2127.8238
-4050 | [7 empty] | -5099.2228
-10570 | [7 empty] | -13308.342
-17780 | [7 empty] | -22386.2176
-28150 | [7 empty] | -35442.7461
-33890 | [7 empty] | -42669.7927
-37810 | [7 empty] | -47605.3368
-37130 | [7 empty] | -46749.171
-30990 | [7 empty] | -39018.4974
-20910 | [7 empty] | -26327.0984
-12330 | [7 empty] | -15524.3005
-5740 | [7 empty] | -7227.0466
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-5890 | [7 empty] | -7415.9067
-1220 | [7 empty] | -1536.0622
-3550 | [7 empty] | -4469.6891
-8970 | [7 empty] | -11293.8342
-20460 | [7 empty] | -25760.5181
-30520 | [7 empty] | -38426.7358
-35700 | [7 empty] | -44948.7047
-41170 | [7 empty] | -51835.8031
-41970 | [7 empty] | -52843.057
-40980 | [7 empty] | -51596.5803
-35080 | [7 empty] | -44168.0829
-25590 | [7 empty] | -32219.5337
-17640 | [7 empty] | -22209.9482
-12100 | [7 empty] | -15234.715
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-12290 | [7 empty] | -15473.9378
-6070 | [7 empty] | -7642.5389
-13220 | [7 empty] | -16644.8705
-18370 | [7 empty] | -23129.0674
-21000 | [7 empty] | -26440.4145
-21960 | [7 empty] | -27649.1192
-24010 | [7 empty] | -30230.2073
-25300 | [7 empty] | -31854.4041
-26360 | [7 empty] | -33189.0155
-27150 | [7 empty] | -34183.6788
-24810 | [7 empty] | -31237.4611
-16620 | [7 empty] | -20925.6995
-8620 | [7 empty] | -10853.1606
-2730 | [7 empty] | -3437.2539
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
16190 | [7 empty] | 12172.6303
16090 | [7 empty] | 12097.4442
9150 | [7 empty] | 6879.5285
2370 | [7 empty] | 1781.9107
0 | [7 empty] | 0
0 | [7 empty] | 0
-1200 | [7 empty] | -1510.8808
-3880 | [7 empty] | -4885.1813
-4630 | [7 empty] | -5829.4819
-2020 | [7 empty] | -2543.3161
-400 | [7 empty] | -503.6269
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
70 | [7 empty] | 52.6303
500 | [7 empty] | 375.9305
110 | [7 empty] | 82.7047
0 | [7 empty] | 0
13400 | [7 empty] | 10074.938
5270 | [7 empty] | 3962.3077
2590 | [7 empty] | 1947.3201
1790 | [7 empty] | 1345.8313
2230 | [7 empty] | 1676.6501
2500 | [7 empty] | 1879.6526
3600 | [7 empty] | 2706.6998
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
40 | [7 empty] | 30.0744
31270 | [7 empty] | 23510.6948
23460 | [7 empty] | 17638.66
14420 | [7 empty] | 10841.8362
7260 | [7 empty] | 5458.5112
3220 | [7 empty] | 2420.9926
990 | [7 empty] | 744.3424
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
750 | [7 empty] | 563.8958
5540 | [7 empty] | 4165.3102
9070 | [7 empty] | 6819.3797
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
22010 | [7 empty] | 16548.4615
15040 | [7 empty] | 11307.9901
5870 | [7 empty] | 4413.4243
350 | [7 empty] | 263.1514
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-480 | [7 empty] | -604.3523
-970 | [7 empty] | -1221.2953
-3070 | [7 empty] | -3865.3368
-3170 | [7 empty] | -3991.2435
-1250 | [7 empty] | -1573.8342
-60 | [7 empty] | -75.544
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
70 | [7 empty] | 52.6303
10 | [7 empty] | 7.5186
0 | [7 empty] | 0
-720 | [7 empty] | -906.5285
-1690 | [7 empty] | -2127.8238
-3870 | [7 empty] | -4872.5907
-9410 | [7 empty] | -11847.8238
-12960 | [7 empty] | -16317.513
-13630 | [7 empty] | -17161.0881
-13900 | [7 empty] | -17501.0363
-11660 | [7 empty] | -14680.7254
-7390 | [7 empty] | -9304.5078
-3860 | [7 empty] | -4860
-1630 | [7 empty] | -2052.2798
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-3330 | [7 empty] | -4192.6943
130 | [7 empty] | 97.7419
90 | [7 empty] | 67.6675
0 | [7 empty] | 0
0 | [7 empty] | 0
-20 | [7 empty] | -25.1813
-190 | [7 empty] | -239.2228
-300 | [7 empty] | -377.7202
-260 | [7 empty] | -327.3575
-190 | [7 empty] | -239.2228
700 | [7 empty] | 526.3027
4040 | [7 empty] | 3037.5186
8760 | [7 empty] | 6586.3027
13010 | [7 empty] | 9781.7122
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
1120 | [7 empty] | 842.0844
2910 | [7 empty] | 2187.9156
4330 | [7 empty] | 3255.5583
5680 | [7 empty] | 4270.5707
6600 | [7 empty] | 4962.2829
8010 | [7 empty] | 6022.4069
49310 | [7 empty] | 37074.268
41280 | [7 empty] | 31036.8238
29380 | [7 empty] | 22089.6774
17500 | [7 empty] | 13157.5682
7770 | [7 empty] | 5841.9603
1210 | [7 empty] | 909.7519
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
280 | [7 empty] | 210.5211
7470 | [7 empty] | 5616.402
13850 | [7 empty] | 10413.2754
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
50 | [7 empty] | 37.5931
1060 | [7 empty] | 796.9727
2090 | [7 empty] | 1571.3896
2960 | [7 empty] | 2225.5087
3460 | [7 empty] | 2601.4392
3930 | [7 empty] | 2954.8139
4320 | [7 empty] | 3248.0397
4390 | [7 empty] | 3300.67
43840 | [7 empty] | 32961.5881
29410 | [7 empty] | 22112.2333
17540 | [7 empty] | 13187.6427
6310 | [7 empty] | 4744.2432
620 | [7 empty] | 466.1538
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-110 | [7 empty] | -138.4974
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
280 | [7 empty] | 210.5211
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
160 | [7 empty] | 120.2978
30 | [7 empty] | 22.5558
0 | [7 empty] | 0
21520 | [7 empty] | 16180.0496
6490 | [7 empty] | 4879.5782
1360 | [7 empty] | 1022.531
350 | [7 empty] | 263.1514
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
28630 | [7 empty] | 21525.7816
19970 | [7 empty] | 15014.665
10020 | [7 empty] | 7533.6476
2550 | [7 empty] | 1917.2457
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-5690 | [7 empty] | -7164.0933
-11130 | [7 empty] | -14013.4197
-8670 | [7 empty] | -10916.114
-3120 | [7 empty] | -3928.2902
-350 | [7 empty] | -440.6736
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
1620 | [7 empty] | 1218.0149
1050 | [7 empty] | 789.4541
0 | [7 empty] | 0
-480 | [7 empty] | -604.3523
-2330 | [7 empty] | -2933.6269
-9290 | [7 empty] | -11696.7358
-13190 | [7 empty] | -16607.0984
-14270 | [7 empty] | -17966.8912
-15350 | [7 empty] | -19326.6839
-15610 | [7 empty] | -19654.0415
-13740 | [7 empty] | -17299.5855
-9880 | [7 empty] | -12439.5855
-5390 | [7 empty] | -6786.3731
-2030 | [7 empty] | -2555.9067
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-4540 | [7 empty] | -5716.1658
-180 | [7 empty] | -226.6321
-1590 | [7 empty] | -2001.9171
-3390 | [7 empty] | -4268.2383
-11840 | [7 empty] | -14907.3575
-18860 | [7 empty] | -23746.0104
-23410 | [7 empty] | -29474.7668
-26150 | [7 empty] | -32924.6114
-27230 | [7 empty] | -34284.4041
-23800 | [7 empty] | -29965.8031
-16870 | [7 empty] | -21240.4663
-6300 | [7 empty] | -7932.1244
-1850 | [7 empty] | -2329.2746
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
540 | [7 empty] | 406.005
31210 | [7 empty] | 23465.5831
27420 | [7 empty] | 20616.0298
17470 | [7 empty] | 13135.0124
5800 | [7 empty] | 4360.794
420 | [7 empty] | 315.7816
0 | [7 empty] | 0
-1040 | [7 empty] | -1309.4301
-4660 | [7 empty] | -5867.2539
-7570 | [7 empty] | -9531.1399
-7750 | [7 empty] | -9757.772
-3330 | [7 empty] | -4192.6943
-920 | [7 empty] | -1158.342
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
30 | [7 empty] | 22.5558
1040 | [7 empty] | 781.9355
2770 | [7 empty] | 2082.6551
4400 | [7 empty] | 3308.1886
41670 | [7 empty] | 31330.0496
36100 | [7 empty] | 27142.1836
26880 | [7 empty] | 20210.0248
17950 | [7 empty] | 13495.9057
10560 | [7 empty] | 7939.6526
5560 | [7 empty] | 4180.3474
940 | [7 empty] | 706.7494
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
1940 | [7 empty] | 1458.6104
7690 | [7 empty] | 5781.8114
12490 | [7 empty] | 9390.7444
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
280 | [7 empty] | 210.5211
2090 | [7 empty] | 1571.3896
3900 | [7 empty] | 2932.2581
5120 | [7 empty] | 3849.5285
6170 | [7 empty] | 4638.9826
6140 | [7 empty] | 4616.4268
6080 | [7 empty] | 4571.3151
46070 | [7 empty] | 34638.2382
35600 | [7 empty] | 26766.2531
30330 | [7 empty] | 22803.9454
25670 | [7 empty] | 19300.273
21390 | [7 empty] | 16082.3077
18220 | [7 empty] | 13698.9082
15760 | [7 empty] | 11849.33
16880 | [7 empty] | 12691.4144
17470 | [7 empty] | 13135.0124
19050 | [7 empty] | 14322.9529
22620 | [7 empty] | 17007.0968
25520 | [7 empty] | 19187.4938
27040 | [7 empty] | 20330.3226
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
220 | [7 empty] | 165.4094
1330 | [7 empty] | 999.9752
2870 | [7 empty] | 2157.8412
5530 | [7 empty] | 4157.7916
8070 | [7 empty] | 6067.5186
9710 | [7 empty] | 7300.5707
11300 | [7 empty] | 8496.0298
12740 | [7 empty] | 9578.7097
13620 | [7 empty] | 10240.3474
11170 | [7 empty] | 8398.2878
5310 | [7 empty] | 3992.3821
43380 | [7 empty] | 32615.732
26160 | [7 empty] | 19668.6849
17840 | [7 empty] | 13413.201
12840 | [7 empty] | 9653.8958
11580 | [7 empty] | 8706.5509
12180 | [7 empty] | 9157.6675
15590 | [7 empty] | 11721.5136
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
700 | [7 empty] | 526.3027
3880 | [7 empty] | 2917.2208
5990 | [7 empty] | 4503.6476
7990 | [7 empty] | 6007.3697
10150 | [7 empty] | 7631.3896
12320 | [7 empty] | 9262.928
13610 | [7 empty] | 10232.8288
14700 | [7 empty] | 11052.3573
16260 | [7 empty] | 12225.2605
62980 | [7 empty] | 47352.2084
53080 | [7 empty] | 39908.7841
39500 | [7 empty] | 29698.5112
26430 | [7 empty] | 19871.6873
16490 | [7 empty] | 12398.1886
10010 | [7 empty] | 7526.129
7950 | [7 empty] | 5977.2953
7560 | [7 empty] | 5684.0695
6410 | [7 empty] | 4819.4293
6590 | [7 empty] | 4954.7643
10140 | [7 empty] | 7623.871
15950 | [7 empty] | 11992.1836
22550 | [7 empty] | 16954.4665
28720 | [7 empty] | 21593.4491
0 | [7 empty] | 0
0 | [7 empty] | 0
2990 | [7 empty] | 2248.0645
8010 | [7 empty] | 6022.4069
10970 | [7 empty] | 8247.9156
13630 | [7 empty] | 10247.866
15990 | [7 empty] | 12022.2581
18260 | [7 empty] | 13728.9826
20240 | [7 empty] | 15217.6675
21400 | [7 empty] | 16089.8263
68360 | [7 empty] | 51397.2208
62930 | [7 empty] | 47314.6154
49600 | [7 empty] | 37292.3077
36640 | [7 empty] | 27548.1886
26940 | [7 empty] | 20255.1365
18350 | [7 empty] | 13796.6501
13270 | [7 empty] | 9977.196
9020 | [7 empty] | 6781.7866
8250 | [7 empty] | 6202.8536
8020 | [7 empty] | 6029.9256
11120 | [7 empty] | 8360.6948
18310 | [7 empty] | 13766.5757
25700 | [7 empty] | 19322.8288
30410 | [7 empty] | 22864.0943
0 | [7 empty] | 0
0 | [7 empty] | 0
990 | [7 empty] | 744.3424
5450 | [7 empty] | 4097.6427
7870 | [7 empty] | 5917.1464
8780 | [7 empty] | 6601.34
9680 | [7 empty] | 7278.0149
10360 | [7 empty] | 7789.2804
10920 | [7 empty] | 8210.3226
11600 | [7 empty] | 8721.5881
56000 | [7 empty] | 42104.2184
45370 | [7 empty] | 34111.9355
33610 | [7 empty] | 25270.0496
23470 | [7 empty] | 17646.1787
15340 | [7 empty] | 11533.5484
10520 | [7 empty] | 7909.5782
6730 | [7 empty] | 5060.0248
640 | [7 empty] | 481.1911
0 | [7 empty] | 0
0 | [7 empty] | 0
70 | [7 empty] | 52.6303
3120 | [7 empty] | 2345.8065
7810 | [7 empty] | 5872.0347
11420 | [7 empty] | 8586.2531
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
26690 | [7 empty] | 20067.1712
17540 | [7 empty] | 13187.6427
7240 | [7 empty] | 5443.4739
110 | [7 empty] | 82.7047
0 | [7 empty] | 0
0 | [7 empty] | 0
-610 | [7 empty] | -768.0311
-9410 | [7 empty] | -11847.8238
-14660 | [7 empty] | -18457.9275
-15730 | [7 empty] | -19805.1295
-12130 | [7 empty] | -15272.487
-4840 | [7 empty] | -6093.886
-710 | [7 empty] | -893.9378
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
22320 | [7 empty] | 16781.5385
18710 | [7 empty] | 14067.3201
12130 | [7 empty] | 9120.0744
4610 | [7 empty] | 3466.0794
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-2770 | [7 empty] | -3487.6166
-5010 | [7 empty] | -6307.9275
-2500 | [7 empty] | -3147.6684
-370 | [7 empty] | -465.8549
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
26610 | [7 empty] | 20007.0223
23280 | [7 empty] | 17503.3251
19910 | [7 empty] | 14969.5533
17970 | [7 empty] | 13510.9429
13760 | [7 empty] | 10345.6079
12580 | [7 empty] | 9458.4119
10220 | [7 empty] | 7684.0199
11910 | [7 empty] | 8954.665
13190 | [7 empty] | 9917.0471
14630 | [7 empty] | 10999.727
16950 | [7 empty] | 12744.0447
18950 | [7 empty] | 14247.7667
20500 | [7 empty] | 15413.1514
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
580 | [7 empty] | 436.0794
1630 | [7 empty] | 1225.5335
2620 | [7 empty] | 1969.8759
3590 | [7 empty] | 2699.1811
4510 | [7 empty] | 3390.8933
5970 | [7 empty] | 4488.6104
6860 | [7 empty] | 5157.7667
6770 | [7 empty] | 5090.0993
5620 | [7 empty] | 4225.4591
46780 | [7 empty] | 35172.0596
39610 | [7 empty] | 29781.2159
35720 | [7 empty] | 26856.4764
33290 | [7 empty] | 25029.4541
33290 | [7 empty] | 25029.4541
34110 | [7 empty] | 25645.9801
35100 | [7 empty] | 26390.3226
0 | [7 empty] | 0
240 | [7 empty] | 180.4467
4040 | [7 empty] | 3037.5186
7090 | [7 empty] | 5330.6948
9410 | [7 empty] | 7075.0124
11260 | [7 empty] | 8465.9553
12970 | [7 empty] | 9751.6377
14310 | [7 empty] | 10759.1315
15560 | [7 empty] | 11698.9578
16920 | [7 empty] | 12721.4888
18010 | [7 empty] | 13541.0174
19080 | [7 empty] | 14345.5087
20500 | [7 empty] | 15413.1514
69260 | [7 empty] | 52073.8958
60600 | [7 empty] | 45562.7792
49760 | [7 empty] | 37412.6055
40320 | [7 empty] | 30315.0372
30490 | [7 empty] | 22924.2432
22300 | [7 empty] | 16766.5012
16690 | [7 empty] | 12548.5608
11020 | [7 empty] | 8285.5087
9610 | [7 empty] | 7225.3846
11220 | [7 empty] | 8435.8809
15650 | [7 empty] | 11766.6253
23170 | [7 empty] | 17420.6203
29950 | [7 empty] | 22518.2382
36300 | [7 empty] | 27292.5558
0 | [7 empty] | 0
1620 | [7 empty] | 1218.0149
8550 | [7 empty] | 6428.4119
11810 | [7 empty] | 8879.4789
14110 | [7 empty] | 10608.7593
16040 | [7 empty] | 12059.8511
17510 | [7 empty] | 13165.0868
18270 | [7 empty] | 13736.5012
18880 | [7 empty] | 14195.1365
19430 | [7 empty] | 14608.66
66890 | [7 empty] | 50291.9851
58860 | [7 empty] | 44254.5409
46470 | [7 empty] | 34938.9826
33940 | [7 empty] | 25518.1638
24560 | [7 empty] | 18465.7072
15760 | [7 empty] | 11849.33
8090 | [7 empty] | 6082.5558
760 | [7 empty] | 571.4144
0 | [7 empty] | 0
20 | [7 empty] | 15.0372
2100 | [7 empty] | 1578.9082
8730 | [7 empty] | 6563.7469
16850 | [7 empty] | 12668.8586
24720 | [7 empty] | 18586.005
0 | [7 empty] | 0
0 | [7 empty] | 0
360 | [7 empty] | 270.67
3870 | [7 empty] | 2909.7022
7160 | [7 empty] | 5383.3251
9590 | [7 empty] | 7210.3474
11420 | [7 empty] | 8586.2531
13240 | [7 empty] | 9954.6402
14780 | [7 empty] | 11112.5062
16170 | [7 empty] | 12157.5931
61910 | [7 empty] | 46547.7171
55020 | [7 empty] | 41367.3945
42120 | [7 empty] | 31668.3871
29010 | [7 empty] | 21811.4888
20710 | [7 empty] | 15571.0422
15580 | [7 empty] | 11713.995
11910 | [7 empty] | 8954.665
10140 | [7 empty] | 7623.871
8590 | [7 empty] | 6458.4864
9050 | [7 empty] | 6804.3424
11400 | [7 empty] | 8571.2159
16390 | [7 empty] | 12323.0025
21710 | [7 empty] | 16322.9032
26200 | [7 empty] | 19698.7593
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
210 | [7 empty] | 157.8908
1590 | [7 empty] | 1195.4591
3510 | [7 empty] | 2639.0323
5150 | [7 empty] | 3872.0844
6640 | [7 empty] | 4992.3573
7930 | [7 empty] | 5962.2581
9110 | [7 empty] | 6849.4541
52640 | [7 empty] | 39577.9653
43830 | [7 empty] | 32954.0695
33660 | [7 empty] | 25307.6427
25910 | [7 empty] | 19480.7196
19080 | [7 empty] | 14345.5087
13610 | [7 empty] | 10232.8288
10170 | [7 empty] | 7646.4268
6200 | [7 empty] | 4661.5385
5870 | [7 empty] | 4413.4243
5090 | [7 empty] | 3826.9727
7400 | [7 empty] | 5563.7717
10680 | [7 empty] | 8029.8759
15010 | [7 empty] | 11285.4342
20140 | [7 empty] | 15142.4814
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
310 | [7 empty] | 233.0769
3860 | [7 empty] | 2902.1836
7070 | [7 empty] | 5315.6576
9510 | [7 empty] | 7150.1985
11570 | [7 empty] | 8699.0323
13440 | [7 empty] | 10105.0124
15180 | [7 empty] | 11413.2506
59650 | [7 empty] | 44848.5112
54630 | [7 empty] | 41074.1687
44620 | [7 empty] | 33548.0397
36980 | [7 empty] | 27803.8213
31260 | [7 empty] | 23503.1762
25300 | [7 empty] | 19022.0844
20370 | [7 empty] | 15315.4094
14680 | [7 empty] | 11037.3201
12310 | [7 empty] | 9255.4094
12660 | [7 empty] | 9518.5608
17050 | [7 empty] | 12819.2308
25380 | [7 empty] | 19082.2333
32710 | [7 empty] | 24593.3747
38500 | [7 empty] | 28946.6501
0 | [7 empty] | 0
3280 | [7 empty] | 2466.1042
10070 | [7 empty] | 7571.2407
13420 | [7 empty] | 10089.9752
15970 | [7 empty] | 12007.2208
18390 | [7 empty] | 13826.7246
20460 | [7 empty] | 15383.0769
22210 | [7 empty] | 16698.8337
23960 | [7 empty] | 18014.5906
25580 | [7 empty] | 19232.6055
26980 | [7 empty] | 20285.2109
76090 | [7 empty] | 57209.1067
71090 | [7 empty] | 53449.8015
60020 | [7 empty] | 45126.6998
49070 | [7 empty] | 36893.8213
38140 | [7 empty] | 28675.9801
28850 | [7 empty] | 21691.1911
22560 | [7 empty] | 16961.9851
19500 | [7 empty] | 14661.2903
19370 | [7 empty] | 14563.5484
22510 | [7 empty] | 16924.3921
29580 | [7 empty] | 22240.0496
35880 | [7 empty] | 26976.7742
39110 | [7 empty] | 29405.2854
0 | [7 empty] | 0
2070 | [7 empty] | 1556.3524
9090 | [7 empty] | 6834.4169
12300 | [7 empty] | 9247.8908
14500 | [7 empty] | 10901.9851
16290 | [7 empty] | 12247.8164
17400 | [7 empty] | 13082.3821
18550 | [7 empty] | 13947.0223
19160 | [7 empty] | 14405.6576
19030 | [7 empty] | 14307.9156
19380 | [7 empty] | 14571.067
19870 | [7 empty] | 14939.4789
18690 | [7 empty] | 14052.2829
15410 | [7 empty] | 11586.1787
59600 | [7 empty] | 44810.9181
37050 | [7 empty] | 27856.4516
25260 | [7 empty] | 18992.0099
17280 | [7 empty] | 12992.1588
15490 | [7 empty] | 11646.3275
16280 | [7 empty] | 12240.2978
18390 | [7 empty] | 13826.7246
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
260 | [7 empty] | 195.4839
2850 | [7 empty] | 2142.804
5630 | [7 empty] | 4232.9777
7550 | [7 empty] | 5676.5509
8580 | [7 empty] | 6450.9677
10120 | [7 empty] | 7608.8337
11840 | [7 empty] | 8902.0347
13010 | [7 empty] | 9781.7122
14310 | [7 empty] | 10759.1315
62260 | [7 empty] | 46810.8685
51890 | [7 empty] | 39014.0695
38670 | [7 empty] | 29074.4665
23810 | [7 empty] | 17901.8114
10440 | [7 empty] | 7849.4293
550 | [7 empty] | 413.5236
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
2400 | [7 empty] | 1804.4665
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
19890 | [7 empty] | 14954.5161
15950 | [7 empty] | 11992.1836
9200 | [7 empty] | 6917.1216
3720 | [7 empty] | 2796.9231
1150 | [7 empty] | 864.6402
110 | [7 empty] | 82.7047
60 | [7 empty] | 45.1117
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
870 | [7 empty] | 654.1191
4370 | [7 empty] | 3285.6328
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
4630 | [7 empty] | 3481.1166
770 | [7 empty] | 578.933
0 | [7 empty] | 0
0 | [7 empty] | 0
-330 | [7 empty] | -415.4922
-1590 | [7 empty] | -2001.9171
-5390 | [7 empty] | -6786.3731
-12060 | [7 empty] | -15184.3523
-15560 | [7 empty] | -19591.0881
-17550 | [7 empty] | -22096.6321
-15400 | [7 empty] | -19389.6373
-8710 | [7 empty] | -10966.4767
-3270 | [7 empty] | -4117.1503
-430 | [7 empty] | -541.399
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
16890 | [7 empty] | 12698.933
16400 | [7 empty] | 12330.5211
9310 | [7 empty] | 6999.8263
1010 | [7 empty] | 759.3797
0 | [7 empty] | 0
-550 | [7 empty] | -692.487
-2660 | [7 empty] | -3349.1192
-10840 | [7 empty] | -13648.2902
-15170 | [7 empty] | -19100.0518
-15260 | [7 empty] | -19213.3679
-9920 | [7 empty] | -12489.9482
-2230 | [7 empty] | -2807.7202
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
210 | [7 empty] | 157.8908
1530 | [7 empty] | 1150.3474
35990 | [7 empty] | 27059.4789
32180 | [7 empty] | 24194.8883
21780 | [7 empty] | 16375.5335
10840 | [7 empty] | 8150.1737
2120 | [7 empty] | 1593.9454
0 | [7 empty] | 0
0 | [7 empty] | 0
-1140 | [7 empty] | -1435.3368
-5410 | [7 empty] | -6811.5544
-6790 | [7 empty] | -8549.0674
-3290 | [7 empty] | -4142.3316
-480 | [7 empty] | -604.3523
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
10 | [7 empty] | 7.5186
820 | [7 empty] | 616.5261
1760 | [7 empty] | 1323.2754
2140 | [7 empty] | 1608.9826
34780 | [7 empty] | 26149.727
25390 | [7 empty] | 19089.7519
18570 | [7 empty] | 13962.0596
11350 | [7 empty] | 8533.6228
5570 | [7 empty] | 4187.866
2160 | [7 empty] | 1624.0199
40 | [7 empty] | 30.0744
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
13510 | [7 empty] | 10157.6427
8490 | [7 empty] | 6383.3002
6740 | [7 empty] | 5067.5434
5280 | [7 empty] | 3969.8263
6510 | [7 empty] | 4894.6154
8070 | [7 empty] | 6067.5186
8840 | [7 empty] | 6646.4516
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
10320 | [7 empty] | 7759.206
3230 | [7 empty] | 2428.5112
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
-1150 | [7 empty] | -1447.9275
-10060 | [7 empty] | -12666.2176
-9790 | [7 empty] | -12326.2694
-9860 | [7 empty] | -12414.4041
-9480 | [7 empty] | -11935.9585
-6680 | [7 empty] | -8410.5699
-3450 | [7 empty] | -4343.7824
-1090 | [7 empty] | -1372.3834
-100 | [7 empty] | -125.9067
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0
0 | [7 empty] | 0

## Sensitivity analysis
Test 5 | Sensitivity analysis on Test 4
[7 empty] | Peak magnitude |  | Thermal conductivity |  | Spacing |  | Ground temperature |  | Boreholes number
Parameter | Value | Units |  |  |  |  | -125758.1 (W) | -153704.4 (W) | 1.5 W/m-K | 2.3W/m-K | 6 m | 10 m | 10 C | 20 C | 3x3 bores | 7x7 bores
Nb | 5×5 | ---- |  | Level | Sizing tool | Borehole length from test 4 | Variation in length | Variation in length | Variation in length | Variation in length | Variation in length | Variation in length | Variation in length | Variation in length | Variation in length | Variation in length
B | 8 | m
D | 4 | m
rb | 75 | mm
rp,o,rp,i | 16.7, 13 | mm |  |  |  | L (m) | % | % | % | % | % | % | % | % | % | %
2dp | 83 | mm | A | L2 | Classic ASHRAE sizing equation | 103.9 | -5.9673 | 5.871 | 14.2445 | -9.5284 | 13.8595 | -6.1598 | -17.0356 | 25.6015 | 176.9971 | -52.9355
mf | 0.074×139.731 | kg.s-1 | B | L2 | Modified ASHRAE sizing equation | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
ρf | 1026 | kg.m-3 | C | L2 | Modified + ASHRAE sizing equation -B | 125.8 | -5.0079 | 4.9285 | 17.0111 | -11.2878 | 11.2878 | -7.4722 | -17.8855 | 26.868 | 144.4356 | -47.5358
cp,f | 4019 | J.kg-1.K-1 | D | L2 | Modified + ASHRAE sizing equation- F | 125.1 | -5.1159 | 4.956 | 17.0264 | -11.3509 | 11.3509 | -7.5939 | -17.9856 | 26.9384 | 145.0839 | -47.8817
μf | 0.00337 | kg.s-1.m-1 | E | L2 | Alternative method | 122.5 | -4.898 | 4.7347 | 16.898 | -11.1837 | 11.5102 | -7.7551 | -18.0408 | 27.102 | 144.9796 | -48
kf | 0.468 | W.m-1.K-1 | Est | L2 | Alternative method (short-term effects) | 118.4 | -4.6453 | 4.4764 | 17.0608 | -11.1486 | 11.9088 | -8.0236 | -18.0743 | 27.1959 | 144.3412 | -48.2264
ρcp,g | 2052 | kJ.m-3.K-1 | F | L2 | GHX design tool box | 93 | -6.4516 | 6.4516 | 8.6022 | -6.4516 | 0 | 0 | -17.2043 | 25.8065 | 177.4194 | -50.5376
ρcp,gr | 3900 | kJ.m-3.K-1 | G | L3 | Modified Ashrae sizing equation -B (monthly) | 125.1 | -3.2774 | 4.8761 | 16.9464 | -11.271 | 11.191 | -7.4341 | -17.8257 | 26.8585 | 144.9241 | -47.6419
ρcp,pipe | 1540 | kJ.m-3.K-1 | H | L3 | Alternative method (monthly) | 121.7 | -3.2868 | 4.848 | 16.8447 | -11.0929 | 11.5037 | -7.6417 | -17.9951 | 23.3361 | 137.6335 | -48.069
αg | 0.08 | m2.day-1 | Hst | L3 | Alternative method (monthly,short-term effects) | 117 | -4.6154 | 4.4444 | 17.0085 | -11.1111 | 11.9658 | -7.9487 | -18.1197 | 27.1795 | 144.7863 | -48.2906
kg | 1.9 | W.m-1.K-1 | I | L3 | EED monthly v.4.17 | 123 | -4.878 | 5.6911 | 12.1951 | -8.1301 | 11.3821 | -6.5041 | -17.8862 | 28.4553 | 150.4065 | -49.2683
kgr | 0.69 | W.m-1.K-1 | J | L3 | GLHEpro monthly v 5.0 | 118.5 | -4.0506 | 4.0928 | 11.2574 | -8.0338 | 11.0042 | -6.5401 | -18.1772 | 28.3544 | 149.4093 | -49.5527
Tg | 15 | °C | K | L4 | EED hourly v.4.17 | 121 | ---- | ---- | 12.3967 | -8.2645 | 13.2231 | -4.1322 | -18.0165 | 32.2314 | 152.8926 | -49.1736
kp | 0.4 | W.m-1.K-1 | L | L4 | DST (COP:Cons.) | 128.9 | ---- | ---- | 8.1265 | -5.9348 | 10.5508 | -7.3894 | -18.0566 | 28.0062 | 141.9511 | -47.6338
TL | 0 | °C | X |  | Your tool
TH | 38 | °C
Rb | 0.2 | m.K.W-1
t | 20 | years
Rc | 0 | m.K.W-1
hconv | 1000 | W.m-2.K-1 |  |  | Mean | 118.7615 | -4.7449 | 5.0337 | 14.2783 | -9.5992 | 10.826 | -6.5073 | -17.8695 | 27.2257 | 150.4046 | -48.8267
q''g | 0 | W/m2
Fsc | 1.04 | -----
COPC | 3.86 | -----
COPH | 4.03 | -----

## nomenclature
Parameter | Symbol | Unit
hourly building or ground loads | qh | (W)
cooling hourly building or ground peak loads | qh,C | (W)
heating hourly building or ground peak loads | qh,H | (W)
monthly building or ground loads | qm | (W)
yearly building or ground loads | qy | (W)
duration of cooling hourly peak loads | th,C | (h)
duration of heating hourly peak loads | th,H | (h)
total number of boreholes | Nb | (---)
distance between the boreholes | B | (m)
distance between the ground surface and the top of boreholes | D | (m)
borehole radius | rb | (mm)
outer and inner radius of U-pipe legs | rp,o,rp,i | (mm)
center-to-center spacing between the legs of a U-tube | 2dp | (mm)
flow rate of the circulating fluid | mf | (kg.s-1)
density of the heat carrier fluid | ρf | (kg.m-3)
specific heat capacity of the circulating fluid | cp,f | (kJ.kg-1K-1)
viscosity of the heat carrier fluid | μf | (Kg.m-1s-1)
fluid thermal conductivity | kf | (W.m-2K-1)
thermal capacity of the soil | ρcp,g | (kJ.m-3K-1)
thermal capacity of the grout | ρcp,gr | (kJ.m-3K-1)
thermal heat capacity of the pipe | ρcp,pipe | (kJ.m-3K-1)
soil thermal diffusivity | αg | (m2.day-1)
soil thermal conductivity | kg | (W.m-1K-1)
thermal conductivity of the backfilling material | kgr | (W.m-1K-1)
initial temperature of the ground | Tg | (°C)
pipe thermal conductivity | kp | (W.m-1K-1)
minimum inlet fluid temperature to the heat pump | TL | (°C)
maximum inlet fluid temperature to the heat pump | TH | (°C)
effective thermal resistance of the boreholes | Rb | (m.K.W-1)
duration of simulation period | t | (yr)
contact thermal resistance | Rc | (m.K.W-1)
internal convection coefficient in pipes | hconv | (W.m-2K-1)
geothermal heat flux | q''g | (W.m-2)
short circuit heat loss factor in the borehole | Fsc | (---)
heat pump coefficient of performances in cooling | COPC | (---)
heat pump coefficient of performances in heating | COPH | (---)